## SZ Abstract (2) (hidden)
Abstract of SZ Plants | [7 empty] | District Wise Cost |  |  | Division Wise Cost |  |  |  | Rehab & O&M Cost
Sr, No | Division | District | Total No of Plants | Functional | Dys Fun + Abundand + Partly Functional | Partly Fun | Dys Fun | Cost of Rehab Plants | 1 Year O&M Cost of all Plants | 3 Year O&M Cost of all Plants | Divisions | Total Cost | 1 Year O&M Cost of all Plants | 3 Year O&M Cost of all Plants | 1 Year O&M Cost Rehab of all Plants | 3 Year O&M Cost of all Plants
1 | Multan | Vehari | 146 | 135 | 11 | 0 | 11 | #REF! | #REF! | #REF! | Multan | #REF! | #REF! | #REF! | #REF! | #REF!
2 |  | Lodhran | 82 | 64 | 18 | 2 | 16 | #REF! | #REF! | #REF!
3 |  | Khanewal | 177 | 157 | 20 | 1 | 19 | #REF! | #REF! | #REF!
4 |  | Multan | 396 | 273 | 123 | 29 | 94 | #REF! | #REF! | #REF!
5 | Bahawalpur | Bahawalpur | 190 | 143 | 47 | 3 | 44 | #REF! | #REF! | #REF! | Bahawalpur | #REF! | #REF! | #REF! | #REF! | #REF!
6 |  | Bahawalnagar | 119 | 98 | 21 | 0 | 21 | #REF! | #REF! | #REF!
7 |  | Rahimyar khan | 203 | 152 | 51 | 0 | 51 | #REF! | #REF! | #REF!
8 | DG Khan | DG Khan | 163 | 63 | 100 | 16 | 84 | #REF! | #REF! | #REF! | DG Khan | #REF! | #REF! | #REF! | #REF! | #REF!
9 |  | Rajanpur | 63 | 26 | 37 | 1 | 36 | #REF! | #REF! | #REF!
10 |  | Layyah | 33 | 14 | 19 | 14 | 5 | #REF! | #REF! | #REF!
11 |  | Muzafargarha | 129 | 22 | 107 | 42 | 65 | #REF! | #REF! | #REF!
Total # of Plants |  |  | 1701 | 1147 | 554 | 108 | 446 | #REF! | #REF! | #REF! | Total | #REF! | #REF! | #REF! | #REF! | #REF!
Average Rehab Cost of Plant |  |  | #REF! |  | Total Rehabilitaion Cost of 554 Plant | [5 empty] | #REF!
Average O&M Cost of Plant for 1 Year |  |  | #REF! |  | Total Cost rehab + O&M of 1 Year for Total 1701 Plants | [5 empty] | #REF!
Average O&M Cost of Plant for 3 Year |  |  | #REF! |  | Total Cost rehab + O&M of 3 Year for Total 1701 Plants | [5 empty] | #REF!
|  |  |  | #REF! | #REF! |  |  |  | #REF!

## SZ Abstract (hidden)
Abstract of SZ Plants | [7 empty] | District Wise Cost |  |  | Division Wise Cost
Sr, No | Division | District | Total No of Plants | Functional | Dys Fun + Abundand + Partly Functional | Partly Fun | Dys Fun | Cost of Rehab Plants | 1 Year O&M Cost of all Plants | 3 Year O&M Cost of all Plants | Divisions | Total Cost | 1 Year O&M Cost of all Plants | 3 Year O&M Cost of all Plants
1 | Multan | Vehari | 146 | 135 | 11 | 0 | 11 | #REF! | #REF! | #REF! | Multan | #REF! | #REF! | #REF!
2 |  | Lodhran | 82 | 64 | 18 | 2 | 16 | #REF! | #REF! | #REF!
3 |  | Khanewal | 177 | 157 | 20 | 1 | 19 | #REF! | #REF! | #REF!
4 |  | Multan | 396 | 273 | 123 | 29 | 94 | #REF! | #REF! | #REF!
5 | Bahawalpur | Bahawalpur | 190 | 143 | 47 | 3 | 44 | #REF! | #REF! | #REF! | Bahawalpur | #REF! | #REF! | #REF!
6 |  | Bahawalnagar | 119 | 98 | 21 | 0 | 21 | #REF! | #REF! | #REF!
7 |  | Rahimyar khan | 203 | 152 | 51 | 0 | 51 | #REF! | #REF! | #REF!
8 | DG Khan | DG Khan | 163 | 63 | 100 | 16 | 84 | #REF! | #REF! | #REF! | DG Khan | #REF! | #REF! | #REF!
9 |  | Rajanpur | 63 | 26 | 37 | 1 | 36 | #REF! | #REF! | #REF!
10 |  | Layyah | 33 | 14 | 19 | 14 | 5 | #REF! | #REF! | #REF!
11 |  | Muzafargarha | 129 | 22 | 107 | 42 | 65 | #REF! | #REF! | #REF!
Total # of Plants |  |  | 1701 | 1147 | 554 | 108 | 446 | #REF! | #REF! | #REF! | Total | #REF! | #REF! | #REF!
Average Rehab Cost of Plant |  |  | #REF! |  | Total Rehabilitaion Cost of 554 Plant | [5 empty] | #REF!
Average O&M Cost of Plant for 1 Year |  |  | #REF! |  | Total Cost rehab + O&M of 1 Year for Total 1701 Plants | [5 empty] | #REF! |  |  | 1518
Average O&M Cost of Plant for 3 Year |  |  | #REF! |  | Total Cost rehab + O&M of 3 Year for Total 1701 Plants | [5 empty] | #REF!

## One Pager (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED BY MCL IN LAHORE
ENGINEERING COST ESTIMATE
Bill No | Description | Qty | Unit Rate (Rs.) | Amount (Rs.) |  |  |  | Total no of Plants
1 | Rehabilitation of Reverse Osmosis 500 LPH | 4 | #REF! | #REF! | 6
2 | Rehabilitation of Media Filtration 2000 LPH | 20 | #REF! | #REF! | 21
3 | Rehabilitation of Ultra Filtration 4000 LPH | 29 | #REF! | #REF! | 14 | Functional Plants Included
4 | Rehabilitation of Ultra Filtration 2000 LPH | 2 | #REF! | #REF! |  |  | #REF!
5 | Rehabilitation of Ultra Filtration 1000 LPH | 3 | 0 | 0 |  | 60475000
6 | Installation of Ultra Filtration 4000 LPH | 4 | 3663400 | 14653600
7 | Installation of Reverese Osmosis 2000 LPH | 1 | 2831355 | 2831355
8 | New Bore Holes | 23.8 | #REF! | #REF! |  |  |  | 0
9 | Washing of Bore Holes | 25.5 | 0 | 0
10 | Rehabilitation of Pre Fab Work | 31.85 | 100000 | 3185000
11 | Rehabilitation of Civil Work | 6 | 71461.1203 | 428766.7215
12 | Water Analysis Reports | 126 | 5100 | 642600 |  |  | Des | Rehab | Abnd | Total Dist Plants | Fun |  |  | 43 | No of Plants |  | 190
Total: - |  |  |  | #REF! |  |  | RO 500 LPH | 0 | 0 |  |  |  |  | RO
6 Months O&M for 63 No. MCL Plants in Lahore Disctrict |  |  |  | 21822102.12
| Total Capital Cost |  |  | #REF! |  |  | RO 1000 LPH | 27 | 2 |  | 5 | Per Plant Avg | 150000 | 30 | RO | 500 LPH | 14
| Add 5% PRA |  |  | #REF! |  |  | RO 2000 LPH | 0 | 1 |  | 0 |  |  | UF | RO | 1000 LPH | 64
| Contingencies & Petty Charges 2% |  |  | #REF! | [7 empty] | Total | 9000000 | 41 | RO | 2000 LPH | 68
| Resident Supervision 1.5% |  |  | #REF!
| Electricity Charges & New Electricity Connections / Outstanding Bills |  |  | 33708000 |  |  | UF 1000 LPH | 0 | [5 empty] | MF | RO | 4000 LPH | 8
| Grand Total |  |  | #REF! |  |  | UF 2000 LPH | 33 | 8 |  | 5 |  |  | 0 | UF | 1000 LPH | 5
[15 empty] | UF | 2000 LPH | 21
Deputy Manager (P&MC) - CZ |  | Director Planning |  |  |  |  | Total | 60 | 11 |  | 10 |  |  |  | MF | 1000 LPH
Punjab Saaf Pani Authroity |  | Punjab Saaf Pani Authroity | [12 empty] | MF | 2000 LPH | 9
[7 empty] | Total | 71 | [6 empty] | MF | 4000 LPH
Chief Engineer /DG Projects | [6 empty] | Functional | 10 | [6 empty] | No of Plants |  | 189
Punjab Saaf Pani Authroity | [6 empty] | Total Plants | 81
[8 empty] | 80 Plants | 0 | 0
[8 empty] | 82 Plants | 86073636.4062 | 86.0736
[8 empty] | Total | 86073636.4062 | 86.0736
[8 empty] | in millions | 86.0736
[8 empty] | Total | 206
[8 empty] | Already Estimated | 80
[8 empty] | Lost | 10
[8 empty] | Rehab by WASA | 34
82
s
24900
35300
RO Feed Pump Repair 4000 LPH
| Repair & maintenance of RO Feed water pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  |  | 46700
23950
36100
44900
RO High Pressure Pump Repair 4000 LPH
| Repair & maintenance of RO High Pressure pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  |  | 56700

## Gen Abstract 6 Months (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED BY MCL IN LAHORE
ENGINEERING COST ESTIMATE
No | Description |  | Amount (Rs.) in Million |  |  | Total no of Plants
1 | REHABILITATION OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED BY MCL IN LAHORE |  | 0 | 0 | 18 | RO | 23 | 11 | 34
| Total Capital Cost |  | 0
| Add 5% PRA |  | 0
| Contingencies & Petty Charges 2% |  | 0 |  | RO 2000 LPH | 19 | 4 |  | 11 |  |  | UF | RO | 1000 LPH | 64
| Resident Supervision 1.5% |  | 0 | [6 empty] | Total | #REF! | 9 | RO | 2000 LPH | 68
| Electricity Charges & New Electricity Connections / Outstanding Bills |  | 13175000
| 6 Months O&M for MCL Plants including 16% PRA |  | 21822102.12
| Grand Total |  | 34997102.12 | #REF! | UF 1000 LPH | 9 | [5 empty] | MF | RO | 4000 LPH | 8
#REF!
|  | Assistant Manager (P&MC) - CZ | [10 empty] | UF | 2000 LPH | 21
|  |  |  | #REF! | MF 2000 LPH | [7 empty] | UF | 4000 LPH | 1
[5 empty] | Total | 28 | 4 |  | 11 |  |  |  | MF | 1000 LPH
[13 empty] | MF | 2000 LPH | 9
Deputy Manager (P&MC) - CZ |  | Director Planning |  |  | Total | 32 | [6 empty] | MF | 4000 LPH
[5 empty] | Functional | 11 | [6 empty] | No of Plants |  | 171
[5 empty] | Total Plants | 43
Chief Engineer/ D.G (O&M) | [5 empty] | 80 Plants | 0 | 0
[6 empty] | 82 Plants | 86073636.4062 | 86.0736
[6 empty] | Total | 86073636.4062 | 86.0736
[6 empty] | in millions | 86.0736
[6 empty] | Total | 206
[6 empty] | Already Estimated | 80
[6 empty] | Lost | 10
[6 empty] | Rehab by WASA | 34
82
s
24900
35300
RO Feed Pump Repair 4000 LPH
| Repair & maintenance of RO Feed water pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  | 46700
23950
36100
44900
RO High Pressure Pump Repair 4000 LPH
| Repair & maintenance of RO High Pressure pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  | 56700

## GA (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATE
No | Description |  | Amount (Rs.) in Million
1 | REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD |  | 0 | 0
| Total Capital Cost |  | 0
| Add 5% PRA |  | 0 | 0
| Contingencies & Petty Charges 2% |  | 0 | 0
| Resident Supervision 1.5% |  | 0
| Electricity Charges & New Electricity Connections / Outstanding Bills |  | 33708000
| O&M for WFP Plants including 16% PRA |  | 0
| Grand Total |  | 33708000
Assistant Manager (P&MC) - CZ
Punjab Saaf Pani Authority
Deputy Manager (P&MC) - CZ |  | Director (P&QC) CZ
Punjab Saaf Pani Authority |  | Punjab Saaf Pani Authority
24900
35300
RO Feed Pump Repair 4000 LPH
| Repair & maintenance of RO Feed water pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  | 46700
23950
36100
44900
RO High Pressure Pump Repair 4000 LPH
| Repair & maintenance of RO High Pressure pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  | 56700

## GS
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No | Description | Qty | Unit Rate (Rs.) | Amount (Rs.)
1 | Rehabilitation of Reverse Osmosis 500 LPH | 1 |  |  | 152 | 152
2 | Rehabilitation of Reverse Osmosis 1000 LPH | 50
3 | Rehabilitation of Reverse Osmosis 2000 LPH | 48
4 | Rehabilitation of Ultra Filtration 4000 LPH | 9
5 | Rehabilitation of Ultra Filtration 2000 LPH | 3
6 | Rehabilitation of Ultra Filtration 1000 LPH | 7
7 | Installation of Ultra Filtration 2000 LPH | 1
8 | Installation of Reverse Osmosis 500 LPH | 4
9 | Installation of Reverse Osmosis 2000 LPH | 9
10 | Installation of Reverse Osmosis 1000 LPH | 6
11 | New Bore Holes | 60
12 | Development of Bore Hole | 40
13 | Injection Well | 12
14 | Rehabilitation of Pre Fab Work (Faisalabad) | 12
15 | Rehabilitation of Civil Work (Faisalabad) | 96
16 | Rehabilitation of Civil Work (Chiniot) | 4
17 | Rehabilitation of Civil Work (Jhang) | 19
18 | Rehabilitation of Civil Work (Toba Tek Singh) | 2
19 | Installation of Pre Fabricated Room (Faisalabad) | 5
20 | Water Analysis Reports | 138
Sub Total
Add 5% PRA
Sub Total (A) (Sub Total + 5% PRA)
06 months O&M for WFP Plants excluding Electricity Charges
Sub Total (B) (06 months O&M)
Add 16% PRA on Sub Total (B)
Sub Total (C) (Sub Total B + 16% PRA)
Grand Total (A+B+C)
24900
35300
RO Feed Pump Repair 4000 LPH
| Repair & maintenance of RO Feed water pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  |  | 46700
23950
36100
44900
RO High Pressure Pump Repair 4000 LPH
| Repair & maintenance of RO High Pressure pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  |  | 56700

## Abstract (hidden)
PUNJAB AAB-E-PAK AUTHORITY
REHABILITATION OF WATER FILTRATION PLANTS IN DISTRICT BAHAWALPUR
Rough Cost Estimate for 47 Dysfunctional & 143 functional Plants: Total 190 Plants
Sr. No | Description | Qty | Per Unit | Amount (Rs.) |  |  | Total no of Plants
1 | REHABLITATION OF RO PLANT 500 LPH | 0 | #REF! | #REF!
2 | #REF! | 20 | #REF! | #REF! |  |  | RO | 31
3 | LAHORE DISTRICT | 7 | #REF! | #REF!
4 | LAHORE DISTRICT | 3 | #REF! | #REF! |  |  | UF | 41 |  |  |  | 3.2432
5 | #REF! | 33 | #REF! | #REF! |  |  | MF | 0
6 | INSTALATION OF RO 500 LPH WFP | 0 | 1258666.5 | 0
7 | LAHORE DISTRICT | 3 | #REF! | #REF!
8 | #REF! | 1 | #REF! | #REF!
9 | #REF! | 5 | #REF! | #REF!
10 | INSTALATION OF MF 2000 LPH WFP | 0 | 669243.75 | 0
11 | New Bore Holes | 7.2 | #REF! | #REF!
12 | Bill No 12:Development of Bore Holes | 7.2 | #REF! | #REF!
13 | Repair of Civil Work | 21.6 | 71461.1203 | 1543560.1974 |  |  |  | #REF!
14 | Injection Well for Brine | 2.7 | 0 | 0
15 | Water Analysis Reports | 144 | 5100 | 734400 |  | Des | Rehab | Abnd | Total Dist Plants | Outstanding Electricity Charges |  |  | 43 | No of Plants |  | 190
Total: - |  |  |  | #REF! | 0 | RO 500 LPH | 0 | 0 |  |  |  |  | RO
| Contingencies & Petty Charges 2% |  |  | 0 |  | RO 1000 LPH | 20 | 3 |  | Per Plant Avg | 150000 |  | 31 | RO | 500 LPH | 14
| Design & Resident Supervision 3% |  |  | 0 |  | RO 2000 LPH | 7 | 1 |  |  |  |  | UF | RO | 1000 LPH | 64
| Electricity Charges |  |  | #REF! | #REF! | #REF! |  |  |  | Total | 9450000 |  | 41 | RO | 2000 LPH | 68
| O&M for 1 Year of 190 Plants in Bahawalpur District |  |  | 116377101.0092 |  | UF 1000 LPH | 3 | [5 empty] | MF | RO | 4000 LPH | 8
| Grand Total |  |  | #REF! |  | UF 2000 LPH | 33 | 5 |  |  |  |  | 0 | UF | 1000 LPH | 5
| Say in million |  |  | #REF! | [9 empty] | UF | 2000 LPH | 21
[6 empty] | MF 2000 LPH | [7 empty] | UF | 4000 LPH | 1
Per Plant Value |  |  |  | #REF! |  | Total | 63 | 9 | [5 empty] | MF | 1000 LPH
[14 empty] | MF | 2000 LPH | 9
[6 empty] | Total Dysfun | 72 | [6 empty] | MF | 4000 LPH
[5 empty] | 0 | Functional | 8 | [6 empty] | No of Plants |  | 190
[5 empty] | 0 | Total Plants | 80
|  |  |  | #REF! | 0
s
24900
35300
RO Feed Pump Repair 4000 LPH
| Repair & maintenance of RO Feed water pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  |  | 46700
23950
36100
44900
RO High Pressure Pump Repair 4000 LPH
| Repair & maintenance of RO High Pressure pump 8000 LPH, for 4000 LPH RO Plant, complete in all respect |  |  | 56700

## RO Rehab 500LPH (hidden)
REHABILITATION OF WATER FILTRATION PLANTS IN DISTRICT BAHAWALPUR | [7 empty] | RO | 0
[8 empty] | Bore | 1
REHABLITATION OF RO PLANT 500 LPH | [7 empty] | Abndd | 2
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR) |  | Dys | 1
1 | N.S | Repair & maintenance of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation | p/job | 0 | 10800 | 0
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | p/job | 0 | 18000 | 0
3 | N.S | Supply Installation & Commissioning of Membrane Housing, Complete in all respect | No. | 0 | 76015 | 0
4 | N.S | Supply Installtion and commissioning of RO Plant membranes(4x40), 2 No. complete in all respect | No. | 0 | 105255 | 0
5 | N.S | Supply Installation and commissioning of RO Feed Pump capacity of 1000 LPH, for 500 LPH RO Plant, complete in all respect | No. | 0 | 73095 | 0
6 | N.S | Supply, Installation and commissioning of RO High Pressure Pump Capacity of 1000 LPH, for 500 LPH RO Plant, complete in all respect | p/job | 0 | 163730 | 0
7 | N.S | Repair & maintenance of RO Feed water pump 1000 LPH, for 500 LPH RO Plant, complete in all respect | p/job | 1 | 28800 | 28800
8 | N.S | Repair & maintenance of RO High Pressure pump 1000 LPH, for 500 LPH RO Plant, complete in all respect | No. | 1 | 40800 | 40800
9 | N.S | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | p/job | 1 | 116365 | 116365
10 | N.S | Supply Installation and Testing of Cartridge Filter complete in all respect | p/job | 0 | 1510 | 0
11 | N.S | Supply Installation and Testing of TDS meter complete with all respects | p/job | 0 | 11695 | 0
12 | N.S | Supply Installation and Testing of Pressure Switchs complete with all respects | p/job | 0 | 16375 | 0
13 | N.S | Supply Installation and testing of Rota meter complete in all respect | p/job | 0 | 7015 | 0
14 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 2 | 9940 | 19880
15 | N.S | Supply Installation and testing of Water meter, complete in all respect | p/job | 0 | 17540 | 0
16 | N.S | Repair & maintenance of water meter including callibration, complete in all respect | p/job | 1 | 6000 | 6000
17 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 1 | 8770 | 8770
18 | N.S | Repair & maintenance of Solinoid valve complete in all respect | p/job | 1 | 4200 | 4200
19 | N.S | Supply Installation & Commissioning of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 1 | 40930 | 40930
20 | N.S | Repair & maintenance of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 1 | 8400 | 8400
21 | N.S | 0 | p/job | 1 | #REF! | #REF!
22 | N.S | Supply, installation and Testing of Chemical Dosing Pump, Chlorinator / Liqued Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank with all repects.complete in all respect | p/job | 1 | 69235 | 69235
23 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, complete in all respects | p/job | 1 | 31575 | 31575
24 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 1 | 6000 | 6000
25 | N.S | Supply and installation of float switch for Water Storage Tank, complete in all respect | kg | 2 | 2925 | 5850
26 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodin No 900-1100 | kg | 30 | 1510 | 45300
27 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect | kg | 80 | 110 | 8800
28 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect | p/job | 80 | 110 | 8800
29 | N.S | Supply installation and commissioning of UV lamp complete in all respect | p/job | 0 | 23390 | 0
30 | N.S | Supply Installation & Commissioning of Manual Valve complete in all respect | p/job | 2 | 3510 | 7020
31 | N.S | Repair & maintenance of Pipe and fittings, complete plant fitting in all respect | no. | 0 | 12000 | 0
32 | N.S | Supply installation & testing of Plastic water Taps with fussion joint, complete in all respect | p/job | 0 | 585 | 0
33 | N.S | Repair & maintenance of Plant control panel with PLC & HMI complete in all respect | p/job | 0 | 36000 | 0
Total Supply & Installtion | [5 empty] | #REF! |  |  | #REF!
PRA 5 % (Total Supply & Installtion) | [5 empty] | #REF! |  |  | #REF! | #REF!
Total Repair & Maintenance | [5 empty] | 157100 |  |  | #REF! | #REF!
PRA 16 % (Total Repair & Maintenance) | [5 empty] | 25136
Total cost of 500LPH Rehab RO Plant Inclusive of Tax | [5 empty] | #REF! | #REF!
Total cost of 500LPH Rehab RO Plant Without Tax | [5 empty] | #REF! | #REF!

## New RO500 (hidden)
REHABILITATION OF WATER FILTRATION PLANTS IN DISTRICT BAHAWALPUR
INSTALATION OF RO 500 LPH WFP
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | Supply installation and commissioning of 500 L/H Reverse Osmosis (RO) Plant for TDS removal up to 5000 mg/l and inclusive of all taxes conforming to standard specifications according to the Punjab Aab-e-Pak Authority. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | No. | 1 | 1198730 | 1198730
| Total Capital |  |  |  | 1198730
| PRA 5% |  |  |  | 59936.5
| Grand Total :- |  |  |  | 1258666.5

## R5
PUNJAB SAAF PANI AUTHORITY | [6 empty] | 0 | RO | 1
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD | [6 empty] | 3 | Bore
BILL OF QUANTITY
Bill No. 1: Rehabilitation of Reverse Osmosis 500 LPH | [6 empty] | 3 No., Plant
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR)
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Stainless Steel | Per Plant | 1
2 | N.S | Supply Installation and commissioning of RO Plant membrane (4x40), including Membrane Housing complete in all respect. Origin: Europe / USA or Equivalent Certification: NSF Pore Size: 0.001 Micron Stablized salt rejection: 99% Capable for TDS: Upto 5000 mg/l Recovery: 15% (each) Life of RO Membrane: 03 to 05 years Pressure Rating: Upto 17 Barg | Per Membrane | 2 |  |  | 45000
3 | N.S | Supply, Installation and commissioning of 1000 LPH High Pressure Pump for 500 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 1000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius | p/job | 1 |  |  |  | 130000
4 | N.S | Rehabilitation of RO Feed water pump 1000 LPH, for 500 LPH RO Plant, complete in all respect | p/job | 1
5 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL | p/job | 1 |  |  | 91365
6 | N.S | Supply Installation and Testing of Cartridge Filter complete in all respect Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE | p/job | 1
7 | N.S | Supply Installation and Testing of Online TDS meter complete with all respects | p/job | 1
8 | N.S | Supply Installation and Testing of Pressure Switches complete with all respects | p/job | 1
9 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equivalent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 2
10 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 3
11 | N.S | Rehabilitation of Analogue Water meter including callibration, complete in all respect. | p/job | 1
12 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 2
13 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 2
14 | N.S | Supply Installation & Commissioning of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 1
15 | N.S | Rehabilitation of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 1
16 | N.S | Supply, installation and Testing of Chemical Dosing Pump / Liquid Dosing Pump with working pressure 4 Bar Imported, along with 80 liter capacity tank complete in all respect Origin: Europe / USA / Asia or Equivalent Pressure: 4 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade | p/job | 1
17 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 1
18 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 1
19 | N.S | Supply and installation of 2 No. electric float switch for Water Storage Tank, complete in all respect | No. | 1 |  |  | 0
20 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 30 |  |  | WASA
21 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 90
22 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel Media | kg | 90
23 | N.S | Supply installation and commissioning of UV lamp rod with quartz complete in all respect Origin: Europe / USA / German or Equivalent | Per Plant | 1
24 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | Per Plant | 1
25 | N.S | Supply installation & testing of Plastic water Taps with fusion joint, complete in all respect | p/job | 5
26 | N.S | Rehabilitation of Plant Control Panel / RO Controller complete in all respect | p/job | 1
27 | N.S | Supply & Installation of FRP Vessel (Size16 X 65) Origin: Europe / USA / German / China or Equivalent | No. | 1
Grand Total
Per Unit Cost = Grand Total

## Bill No 2 RO 2000 Rehab (hidden)
PUNJAB SAAF PANI AUTHORITY | [7 empty] | 21013737 | RO | 1
[8 empty] | 957635 | Bore
LAHORE DISTRICT | [7 empty] | 20056102 | Dys
BILL OF QUANTITY | [8 empty] | fun
Bill No. 2: Rehabilitation of Reverse Osmosis 2 m3/hr
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR) |  |  |  | #REF!
1 | N.S | Repair & maintenance of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation | p/job | 1 | 10800 | 10800
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | p/job | 0 | 18000 | 0
3 | N.S | Supply Installation & Commissioning of Membrane Housing, Complete in all respect | No. | 0 | 76015 | 0
4 | N.S | Supply Installtion and commissioning of RO Plant membranes(4x40), 4 No. complete in all respect. inclusive of Carriage to Site and Labor for Installation | No. | 1 | 421015 | 421015
5 | N.S | Supply Installation and commissioning of RO Feed Pump capacity of 4000 LPH, for 2000 LPH RO Plant, complete in all respect | No. | 0 | 119290 | 0
6 | N.S | Supply, Installation and commissioning of RO High Pressure Pump Capacity of 4000 LPH, for 2000 LPH RO Plant, complete in all respect | p/job | 0 | 239745 | 0
7 | N.S | Repair & maintenance of RO Feed water pump 2000 LPH, for 1000 LPH RO Plant, complete in all respect | p/job | 1 | 28800 | 28800
8 | N.S | Repair & maintenance of RO High Pressure pump 4000 LPH, for 2000 LPH RO Plant, complete in all respect | No. | 1 | 40800 | 40800
9 | N.S | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | p/job | 0 | 116365 | 0
10 | N.S | Supply Installation and Testing of Cartridge Filter complete in all respect | p/job | 1 | 1510 | 1510
11 | N.S | Supply Installation and Testing of TDS meter complete with all respects | p/job | 1 | 11695 | 11695
12 | N.S | Supply Installation and Testing of Pressure Switchs complete with all respects | p/job | 1 | 16375 | 16375
13 | N.S | Supply Installation and testing of Rota meter complete in all respect | p/job | 1 | 7015 | 7015
14 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 2 | 9940 | 19880
15 | N.S | Supply Installation and testing of Water meter, complete in all respect | p/job | 0 | 17540 | 0
16 | N.S | Repair & maintenance of water meter including callibration, complete in all respect | p/job | 1 | 6000 | 6000
17 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 0 | 8770 | 0
18 | N.S | Repair & maintenance of Solinoid valve complete in all respect | p/job | 1 | 4200 | 4200
19 | N.S | Supply Installation & Commissioning of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 0 | 40930 | 0
20 | N.S | Repair & maintenance of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 2 | 8400 | 16800
21 | N.S | Supply, installation and Testing of Chemical Dosing Pump, Chlorinator / Liqued Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank with all repects.complete in all respect | p/job | 1 | 69235 | 69235
22 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, complete in all respects | p/job | 0 | 31575 | 0
23 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 1 | 6000 | 6000
24 | N.S | Supply and installation of float switch for Water Storage Tank, complete in all respect | No. | 1 | 2925 | 2925
25 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodin No 900-1100 | kg | 128 | 1510 | 193280
26 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect | kg | 128 | 110 | 14080
27 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect | kg | 128 | 110 | 14080
28 | N.S | Supply installation and commissioning of UV lamp complete in all respect | p/job | 1 | 23390 | 23390
29 | N.S | Supply Installation & Commissioning of Manual Valve complete in all respect | p/job | 0 | 3510 | 0
30 | N.S | Repair & maintenance of Pipe and fittings, complete plant fitting in all respect | no. | 1 | 12000 | 12000
31 | N.S | Supply installation & testing of Plastic water Taps with fussion joint, complete in all respect | p/job | 3 | 585 | 1755
32 | N.S | Repair & maintenance of Plant control panel with PLC & HMI complete in all respect | p/job | 1 | 36000 | 36000
Grand Total | [5 empty] | 957635
Total Supply & Installtion | [5 empty] | #REF! |  |  |  | 921635
PRA 5 % (Total Supply & Installtion) | [5 empty] | #REF! |  |  |  | 46081.75 | 967716.75
Total Repair & Maintenance | [5 empty] | 382840 |  |  |  | 147461.6 | 1069096.6
PRA 16 % (Total Repair & Maintenance) | [5 empty] | 61254.4
Total cost of 2000LPH Rehab RO Plant Inclusive of Tax | [5 empty] | #REF! | #REF!
Total cost of 2000LPH Rehab RO Plant Without Tax | [5 empty] | #REF! | #REF!
|  |  | Per Unit Cost |  |  | 957635
Assistant Manager (P&MC) - CZ |  |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  |  | Punjab Aab-e-Pak Authority

## Bill No 3 UF 1000 Rehab (hidden)
PUNJAB SAAF PANI AUTHORITY | [7 empty] | 3460870 | UF | #REF!
[8 empty] | 0 | abnd | 0
LAHORE DISTRICT | [7 empty] | 3460870 | dys | 2
BILL OF QUANTITY
Bill No. 3: Rehabilitation of Ultra Filtration 1 m3/hr
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR)
1 | N.S | Repair & maintenance of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation | p/job | 3 | 10800 | 32400
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | p/job | 2 | 18000 | 36000
3 | N.S | Supply Installation and commissioning of UF Feed Pump capacity of 1000 LPH, for 1000 LPH UF Plant, complete in all respect | No. | 1 | 73095 | 73095
4 | N.S | Repair & maintenance of UF Feed water pump 1000 LPH, for 1000 LPH UF Plant, complete in all respect | p/job | 1 | 28800 | 28800
5 | N.S | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | p/job | 1 | 116365 | 116365
6 | N.S | Supply and installation of safety filter strainer | p/job | 9 | 1405 | 12645
7 | N.S | Supply Installation and Testing of TDS meter complete with all respects | p/job | #REF! | 11695 | #REF!
8 | N.S | Supply Installation and Testing of Pressure Switchs complete with all respects | p/job | 9 | 16375 | 147375
9 | N.S | Supply Installation and testing of Rota meter complete in all respect | p/job | 9 | 7015 | 63135
10 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 18 | 9940 | 178920
11 | N.S | Supply Installation and testing of Water meter, complete in all respect | p/job | 3 | 17540 | 52620
12 | N.S | Repair & maintenance of water meter including callibration, complete in all respect | p/job | 5 | 6000 | 30000
13 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 6 | 8770 | 52620
14 | N.S | Repair & maintenance of Solinoid valve complete in all respect | p/job | 5 | 4200 | 21000
15 | N.S | Supply Installation & Commissioning of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 3 | 40930 | 122790
16 | N.S | Repair & maintenance of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 5 | 8400 | 42000
17 | N.S | Supply, installation and Testing of Chemical Dosing Pump, Chlorinator / Liqued Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank with all repects.complete in all respect | p/job | #REF! | 69235 | #REF!
18 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, complete in all respects | p/job | 1 | 31575 | 31575
19 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 17 | 6000 | 102000
20 | N.S | Supply and installation of float switch for Water Storage Tank, complete in all respect | kg | 2 | 2925 | 5850
21 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodin No 900-1100 | kg | #REF! | 1510 | #REF!
22 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect | kg | #REF! | 110 | #REF!
23 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect | p/job | #REF! | 110 | #REF!
24 | N.S | Replacement of Granular Feric Oxide use for druinking water treatment with oxidation capavity of AS3 to AS5, commissioning complete in all respect | kg | 160 | 2640 | 422400
25 | N.S | Supply installation and commissioning of UV lamp complete in all respect | p/job | #REF! | 23390 | #REF!
26 | N.S | Supply Installation & Commissioning of Manual Valve complete in all respect | p/job | 1 | 3510 | 3510
27 | N.S | Repair & maintenance of Pipe and fittings, complete plant fitting in all respect | no. | #REF! | 12000 | #REF!
28 | N.S | Supply installation & testing of Plastic water Taps with fussion joint, complete in all respect | p/job | #REF! | 585 | #REF!
29 | N.S | Repair & maintenance of Plant control panel with PLC & HMI complete in all respect | p/job | #REF! | 36000 | #REF!
Grand Total | [5 empty] | 0
Total Supply & Installtion | [5 empty] | #REF! |  |  |  | #REF!
PRA 5 % (Total Supply & Installtion) | [5 empty] | #REF! |  |  |  | #REF! | #REF!
Total Repair & Maintenance | [5 empty] | #REF! |  |  |  | #REF! | #REF!
PRA 16 % (Total Repair & Maintenance) | [5 empty] | #REF!
Total cost of 1000LPH Rehab UF Plant Inclusive of Tax | [5 empty] | #REF! | #REF!
Total cost of 1000LPH Rehab UF Plant Without Tax | [5 empty] | #REF! | #REF!
|  |  | Per Unit Cost |  |  | #REF!
Assistant Manager (P&MC) - CZ |  |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  |  | Punjab Aab-e-Pak Authority

## R1
PUNJAB SAAF PANI AUTHORITY | [6 empty] | 0 | RO | 50
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD | [6 empty] | 0 | Bore
BILL OF QUANTITY
Bill No. 2: Rehabilitation of Reverse Osmosis 1000 LPH
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR)
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Stainless Steel | Per Plant | 30 |  |  | 10800
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | Per Plant | 20 |  |  | 19000
3 | N.S | Supply Installation and commissioning of RO Plant membrane (4x40), including Membrane Housing complete in all respect. Origin: Europe / USA or Equivalent Certification: NSF Pore Size: 0.001 Micron Stablized salt rejection: 99% Capable for TDS: Upto 5000 mg/l Recovery: 15% (each) Life of RO Membrane: 03 to 05 years Pressure Rating: Upto 17 Barg | Per Membrane | 80 |  |  | 52627.5 | 10 | 10 | 20
4 | N.S | Supply Installation and commissioning of 2000 LPH Feed Pump for 1000 LPH RO WFP, complete in all respect Discharge: 2000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / China or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 06 Barg Pump Efficiency: ≥ 40% Motor Starter: DOL | No. | 15 |  |  | 94745 | 80000
5 | N.S | Supply, Installation and commissioning of 2000 LPH High Pressure Pump for 1000 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 2000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius | p/job | 15 |  |  | 204660 | 130000
6 | N.S | Rehabilitation of RO Feed water pump 2000 LPH, for 1000 LPH RO Plant, complete in all respect | p/job | 35 |  |  | 18800
7 | N.S | Rehabilitation of RO High Pressure pump 2000 LPH, for 1000 LPH RO Plant, complete in all respect | p/job | 35 |  |  | 35800
8 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL | p/job | 25 |  |  | 91365
9 | N.S | Supply Installation and Testing of Cartridge Filter complete in all respect Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE | p/job | 50 |  |  | 1510
10 | N.S | Supply Installation and Testing of Online TDS meter complete with all respects | p/job | 50 |  |  | 8695
11 | N.S | Supply Installation and Testing of Pressure Switches complete with all respects | p/job | 50 |  |  | 6375
12 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equivalent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 50 |  |  | 5117
13 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 200 |  |  | 3400
14 | N.S | Supply Installation and testing of Analogue Water meter, complete in all respect | p/job | 25 |  |  | 17540
15 | N.S | Rehabilitation of analogue water meter including callibration, complete in all respect | p/job | 25 |  |  | 6000
16 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 50 |  |  | 8500
17 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 60 |  |  | 3200
18 | N.S | Supply Installation & Commissioning of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 30 |  |  | 40930
19 | N.S | Rehabilitation of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 50 |  |  | 8400
20 | N.S | Supply, installation and Testing of Chemical Dosing Pump / Liquid Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank complete in all respect Origin: Europe / USA / Asia or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade | p/job | 25 |  |  | 69235
21 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 35 |  |  | 45575
22 | N.S | Chemical Cleaning of Water Storage tank, complete in all respects at site | p/job | 65 |  |  | 2500
23 | N.S | Supply and installation of 2 No. electric float switch for Water Storage Tank, complete in all respect | No. | 28 |  |  | 3625
24 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 1200 |  |  | 1510
25 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 3150 |  |  | 70
26 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel Media | kg | 2700 |  |  | 70
27 | N.S | Supply installation and commissioning of UV lamp rod with quartz complete in all respect Origin: Europe / USA / German or Equivalent | Per Plant | 20 |  |  | 11390
28 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | Per Plant | 25 |  |  | 22000
29 | N.S | Supply installation & testing of Plastic water Taps with fusion joint, complete in all respect | p/job | 250 |  |  | 585
30 | N.S | Rehabilitation of Plant Control Panel / RO Controller complete in all respect | p/job | 25 |  |  | 36000
31 | N.S | Supply & Installation of FRP Vessel (Size16 X 65) Origin: Europe / USA / German / China or Equivalent | No. | 1
Grand Total
Per Unit Cost = Grand Total / 50

## R2
PUNJAB SAAF PANI AUTHORITY | [7 empty] | RO | 48
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No. 3: Rehabilitation of Reverse Osmosis 2000 LPH
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR)
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Frame stainless steel | p/job | 30 |  |  |  |  | 30%
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | p/job | 20 |  |  |  |  | 30%
3 | N.S | Supply Installation and commissioning of RO Plant membrane (4x40), including Membrane Housing complete in all respect. Origin: Europe / USA or Equivalent Certification: NSF Pore Size: 0.001 Micron Stablized salt rejection: 99% Capable for TDS: Upto 5000 mg/l Recovery: 15% (each) Life of RO Membrane: 03 to 05 years Pressure Rating: Upto 17 Barg | Per Membrane | 160 |  |  |  |  | 2000% | 20
4 | N.S | Supply Installation and commissioning of 4000 LPH Feed Pump for 2000 LPH RO WFP, complete in all respect Discharge: 4000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / China or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 06 Barg Pump Efficiency: ≥ 40% Motor Starter: DOL | No. | 20 |  |  |  |  | 10%
5 | N.S | Supply, Installation and commissioning of 4000 LPH High Pressure Pump for 2000 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 4000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius | p/job | 20 |  |  |  |  | 10%
6 | N.S | Rehabilitation of RO Feed water pump 2000 LPH, for 1000 LPH RO Plant, complete in all respect | p/job | 28 |  |  |  |  | 30%
7 | N.S | Rehabilitation of RO High Pressure pump 4000 LPH, for 2000 LPH RO Plant, complete in all respect | No. | 28 |  |  |  |  | 30%
8 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL | p/job | 20 |  |  |  |  | 10%
9 | N.S | Supply Installation and Testing of Cartridge Filter complete in all respect Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE | p/job | 38 |  |  |  |  | 100%
10 | N.S | Supply Installation and Testing of online TDS meter complete with all respects | p/job | 38 |  |  |  |  | 60%
11 | N.S | Supply Installation and Testing of Pressure Switchs complete with all respects | p/job | 38 |  |  |  |  | 40%
12 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 38 |  |  |  |  | 60%
13 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 192 |  |  |  |  | 200%
14 | N.S | Supply Installation and testing of analogue Water meter, complete in all respect | p/job | 15 |  |  |  |  | 20%
15 | N.S | Rehabilitation of analogue water meter including callibration, complete in all respect | p/job | 33 |  |  |  |  | 50%
16 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 96 |  |  |  |  | 50%
17 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 48 |  |  |  |  | 100%
18 | N.S | Supply Installation & Commissioning of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 42 |  |  |  |  | 10%
19 | N.S | Rehabilitation of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 28.8 |  |  |  |  | 60% |  | 96
20 | N.S | Supply, installation and Testing of Chemical Dosing Pump / Liquid Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank complete in all respect Origin: Europe / USA / Asia or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade | p/job | 20
21 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 12
22 | N.S | Chemical Cleaning & repair of Water Storage tanks, complete in all respects at site | p/job | 36
23 | N.S | Supply and installation of 2 No. float switch for Water Storage Tank, complete in all respect | kg | 24 |  |  |  |  | 50%
24 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 1440 |  |  |  |  | 50
25 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 5376 |  |  |  |  | 160
26 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel media | p/job | 4608 |  |  |  |  | 160
27 | N.S | Replacement of Granular Feric Hydroxide use for drinking water treatment with oxidation capacity of As3 to As5, commissioning complete in all respect Operating Pressure: 1.5 - 3 Bar Media: Grannular Ferric Hydroxide Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 3072
28 | N.S | Supply installation and commissioning of UV lamp rod with quartz complete in all respect Origin: Europe / USA / German or Equivalent | p/job | 20 |  |  |  |  | 100%
29 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | no. | 25 |  |  |  |  | 50%
30 | N.S | Supply installation & testing of Plastic water Taps with fussion joint, complete in all respect | p/job | 240 |  |  |  |  | 5
31 | N.S | Rehabilitation of Plant Control Panel / RO Controller complete in all respect | p/job | 25 |  |  |  |  | 100%
32 | N.S | Supply & Installation of FRP Vessel (Size24 X 72) Origin: Europe / USA / German / China or Equivalent | No. | 1
Grand Total | [6 empty] | 0
Per Unit Cost = Grand Total / 48

## UF 1 Rehab (hidden)
PUNJAB SAAF PANI AUTHORITY | [6 empty] | 39402793 | UF | 2
[7 empty] | 0 | Abnd
LAHORE DISTRICT | [6 empty] | 39402793 | fed
BILL OF QUANTITY | [7 empty] | Dys
Bill No. 2: Rehabilitation of Ultra Filtration 1000 LPH | [7 empty] | fun
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR) |  |  | #REF!
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Frame stainless steel | Per Plant | 2 | 10800 | 21600
2 | N.S | Membranes recovery (minimum 50%) with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | Per Plant | 1 | 19000 | 19000
3 | N.S | Supply, Installation & Commissioning of UF membrane/s Material of vessel: uPVC Removal Size: 0.02 Micron Manufacturer Type: Mutibore (seven bore) Manufecturer: GE Power (IMT) / INGE or Equivalent Filter vessel: uPVC Thickness: 5mm Membrane material: PES (Polystyrene) Countery Made: Europe / USA / Germany or Equivalent. Membrane Working pressure: 5 Bar Max Membrane Life: 5 years Bacterail Removal Effciency of UF membrane: 99.9999% log 6 Viruses Removal effciency of the UF membrane: 99.99% log 4 Auto Back wash Working pressure: 0-2 Bar Working temprature: Max 40 degree Celsius | Per Plant | 1 | 304070 | 304070 |  | 45000
4 | N.S | Supply Installation and commissioning of UF Feed Pump capacity of 4000 LPH, for 2000 LPH UF Plant, complete in all respect Operating Pressure: 2m3/h at minimum 10 m head, efficiency > 60% Sand Filter: Sand Filter with automatic Backwash Active Carbon Filter: Active Carbon Filter with automatic backwash | No. | 1 | 94745 | 94745 |  | 80000
5 | N.S | Supply Installation and commissioning of UF Back Wash Pump capacity of 4000 LPH, for 2000 LPH UF Plant, complete in all respect Operating Pressure: 2m3/h at minimum 10 m head, efficiency > 60% Sand Filter: Sand Filter with automatic Backwash Active Carbon Filter: Active Carbon Filter with automatic backwash | No. | 1 | 94745 | 94745
6 | N.S | Rehabilitation of UF Feed water pump 4000 LPH, for 2000 LPH UF Plant, complete in all respect | p/job | 1 | 18800 | 18800
7 | N.S | Rehabilitation of UF Feed water pump 4000 LPH, for 2000 LPH UF Plant, complete in all respect | p/job | 1 | 18800 | 18800
8 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Origin: Europe / USA / German / Pakistan or Equivalent Pump Type: Submersible Pump Impeller Type: SS 304 Pump Efficiency: >60% Motor Starter: Star Delta | p/job | 1 | 91365 | 91365
9 | N.S | Supply and installation of safety filter strainer | p/job | 2 | 8405 | 16810
10 | N.S | Supply Installation and Testing of Online TDS meter complete with all respects | p/job | 2 | 8695 | 17390
11 | N.S | Supply Installation and Testing of Pressure Switches complete with all respects | p/job | 2 | 6375 | 12750
12 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 4 | 5117 | 20468
13 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 6 | 3400 | 20400
14 | N.S | Supply Installation and testing of Analogue Water meter, complete in all respect | p/job | 2 | 17540 | 35080
15 | N.S | Rehabilitation of Analogue Water meter including callibration, complete in all respect | p/job | 0 | 6000 | 0
16 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 8 | 8500 | 68000
17 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 4 | 3200 | 12800
18 | N.S | Supply Installation & Commissioning of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 5 | 40930 | 204650
19 | N.S | Rehabilitation of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 0 | 8400 | 0
20 | N.S | Supply, installation and Testing of Chlorine Dosing Pump with working pressure 5 - 7 Bar imported, along with 80 liter capacity tank with all repects.complete in all respect Origin: Europe / USA / German or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Material: PVDF | p/job | 3 | 89235 | 267705
21 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 2 | 45575 | 91150
22 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 4 | 2500 | 10000
23 | N.S | Supply and installation of electric float switch for Water Storage Tank, complete in all respect No: 02 | No. | 6 | 3625 | 21750
24 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 48 | 1510 | 72480
25 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 120 | 70 | 8400
26 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel Media | kg | 120 | 70 | 8400
27 | N.S | Replacement of Granular Feric Hydroxide use for drinking water treatment with oxidation capacity of As3 to As5, commissioning complete in all respect Operating Pressure: 1.5 - 3 Bar Media: Grannular Ferric Hydroxide Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 120 | 2510 | 301200 | WASA
26 | N.S | Supply Installation & Commissioning of Manual Valve 3Way complete in all respect | p/job | 0 | 22210 | 0
27 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | Per Plant | 2 | 22000 | 44000
28 | N.S | Supply installation & testing of Plastic water Taps with fusion joint, complete in all respect | p/job | 6 | 585 | 3510
29 | N.S | Rehabilitation of Plant control panel with PLC & HMI complete in all respect | Per Plant | 2 | 46000 | 92000
Grand Total | [6 empty] | #REF!
|  |  | Per Unit Cost |  |  | 0 | #REF!
Assistant Manager (P&MC) - CZ |  |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  |  | Punjab Aab-e-Pak Authority

## U4
PUNJAB SAAF PANI AUTHORITY | [6 empty] | 39402793 | UF | 9
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD | [6 empty] | 0 | Abnd
BILL OF QUANTITY | [7 empty] | Dys
Bill No. 4: Rehabilitation of Ultra Filtration 4000 LPH | [7 empty] | fun
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR) |  |  | #REF!
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Frame stainless steel | Per Plant | 9 |  |  | 10800
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | Per Plant | 5 |  |  | 19000
3 | N.S | Supply, Installation & Commissioning of UF membrane including membrane housing complete in all respect Origin: Europe / USA or Equivalent. Removal Size: 0.02 Micron Certification: NSF Material of vessel: uPVC Thickness: 5mm Membrane material: PVDF (Polyvinylidene flouride)/ PES (Polyethersulfone) - Multibore technology Membrane Working pressure: upto 5 Bar Membrane Life: Minimum 5 years Bacterail Removal effciency of UF membrane: 99.9999% log 6 Viruses Removal effciency of UF membrane: 99.99% log 4 Auto Backwash enabled Working temprature: Max 40 degree Celsius | Per Plant | 4 |  |  | 1216280 | 45000
4 | N.S | Supply Installation and commissioning of 4000 LPH Feed Pump for 4000 LPH UF WFP, complete in all respect Origin: Europe / USA / Asia or Equivalent Discharge: 4000 LPH Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 05 Barg Pump Efficiency: > 40% Motor Starter: DOL | No. | 5 |  |  | 94745 | 80000
5 | N.S | Rehabilitation of UF Feed water pump 4000 LPH, for 4000 LPH UF Plant, complete in all respect | p/job | 4 |  |  | 18800
6 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. Discharge: 3000-5000 LPHSupply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL | p/job | 4 |  |  | 91365
7 | N.S | Supply and installation of S.S safety filter strainer | p/job | 9 |  |  | 8405
8 | N.S | Supply Installation and Testing of Pressure Switches complete with all respects | p/job | 9 |  |  | 6375
9 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 18 |  |  | 5117
10 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 27 |  |  | 3400
11 | N.S | Supply Installation and testing of Analogue Water meter, complete in all respect | p/job | 9 |  |  | 17540
12 | N.S | Rehabilitation of Analogue Water meter including callibration, complete in all respect | p/job | 0 |  |  | 6000
13 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 18 |  |  | 8500
14 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 18 |  |  | 3200
15 | N.S | Supply Installation & Commissioning of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 9 |  |  | 40930
16 | N.S | Rehabilitation of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 9 |  |  | 8400
17 | N.S | Supply, installation and Testing of Chlorine Dosing Pump with working pressure 5 - 7 Bar imported, along with 80 liter capacity tank with all repects.complete in all respect Origin: Europe / USA / Asia or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Material: PVDF | p/job | 4 |  |  | 89235
18 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 9 |  |  | 45575
19 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 9 |  |  | 2500
20 | N.S | Supply and installation of 2 No. electric float switch for Water Storage Tank, complete in all respect | No. | 9 |  |  | 3625
21 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 324 |  |  | 1510
22 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 2394 |  |  | 70
23 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel Media | kg | 2052 |  |  | 70
24 | N.S | Replacement of Granular Feric Hydroxide use for drinking water treatment with oxidation capacity of As3 to As5, commissioning complete in all respect Operating Pressure: 1.5 - 3 Bar Media: Grannular Ferric Hydroxide Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 1152 |  |  | 2510
25 | N.S | Supply installation and commissioning of UV lamp rod with quartz complete in all respect Origin: Europe / USA / German or Equivalen | No. | 4
26 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | Per Plant | 5 |  |  | 22000
27 | N.S | Supply installation & testing of Plastic water Taps with fusion joint, complete in all respect | p/job | 45 |  |  | 585
28 | N.S | Rehabilitation of Plant control panel with PLC & HMI complete in all respect | Per Plant | 5 |  |  | 46000
29 | N.S | Supply & Installation of FRP Vessel (Size24 X 72) Origin: Europe / USA / German / China or Equivalent | No. | 1
Grand Total
Per Unit Cost = Grand Total / 9

## B3 R1 New (hidden)
PUNJAB SAAF PANI AUTHORITY
LAHORE DISTRICT
ENGINEERING COST ESTIMATE
Bill No 3 : Installation of Reverse Osmosis 1000 LPH
RO 1000 LPH Plant
Sr. No | Description | Qty | Unit Rate (Rs) | Amount (Rs)
1 | Supply, transport, erection, installation, testing & commissioning of 1,000 L/H Reverse Osmosis (RO) Plant for TDS removal along with all other contaminants, including carriage, loading/unloading charges inclusive of all taxes conforming to Mentioned in Technical specifications of filtration plants. Control PLC GSM/GPRS/ SCADA enabled. The unit should be composed of Raw and Product water tanks (1000 Liter capacity for each) Feed and High Pressure Pump, pressure gauges, variable area flow meter for raw water and for product water totalizer/ water meter, pressure safety switch and valves, Multiport valves, safety filter strainers/cartridges filter, sand filter, carbon filters. System should be fully automatic. Provission of UV system, Anti secalent system with Anti scalent PVDF based dosing Pumps and chemical tank. The complete plant should be able to operate/backwash automatically through Automatic Multiport Valve operated by PLC with same feed pump based system. All type of piping and instrumentation shall be considered as part of filtration plant complete in all respect. The plant should be supplied to provide the treated water as per the WHO limits (strict compliance). The specifications along with equipment and accessories properly mounted in the frame/skid are given below: | 1 | 2129660 | 2129660
2 | Raw Water Feed Pump
Discharge: 2000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / German / Pakistan or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: SS 304 Discharge: As per the capacity of Plant (2000 LPH) Operating Head: Up to 06 Barg Pump Efficiency: >60% Motor Starter: Star Delta
3 | Submersible Pump
Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Origin: Europe / USA / German / Pakistan or Equivalent Pump Type: Submersible Pump Impeller Type: SS 304 Discharge: As per the capacity of Plant (2000 LPH) Pump Efficiency: >60% Motor Starter: Star Delta
4 | Pre-Filtration
4 (a) | Sand Filter
Material: FRP Origin: Europe / USA / German or Equivalent Fitration Rate: 6 - 15 m/hr Vessel Certification: NSF Operating Pressure Max: Up to 06 Barg
4 (b) | Filter Media Sand
Material: Quartz Silica Sand Origin: Europe / USA / German or Equivalent Size of Media: 0.6 - 0.8 mm Cleaning Process: Automatic, through PLC / Time Controller MPV
4 (c) | Activated Carbon Filter
Material: FRP Origin: Europe / USA / German or Equivalent Media & Vessel Certification: NSF Fitration Rate: 5 - 15 m/hr Operating Pressure Max: Up to 06 Barg
4 (d) | Filter Media Carbon
Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
4 (e) | Cartridge Filter
Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE
5 | RO Skid
Frame: Stainless Steel
6 | High Pressure Pump multistage
Discharge: 2000 LPH Operating Head: Upto 06 Barg Pump Type: Vertical High Pressure Pump Origin: Europe / USA / German or Equivalent Impeller material: S.S. 304 Pump Efficiency: >60% Motor Starter: Star Delta Motor Temperature Class: 45 degree Celsius Make: Lewara / Grundfous / KSB / CNP / Vilo or Equivalent
7 | RO Housing
Material: FRP Certification: NSF
8 | RO Membrane
Origin: Europe / USA / German or Equivalent (Assembly of Parts may be Pakistan) No. of Stages: Up to 2 No. of Membranes: Up to 4 Certification: NSF Stable salt rejection: Minimum - 99% Capacity: 1000 LPH For Permeate water Capable for TDS: Upto 5000 mg/l Recovery: Should be More than 50% Ambient Temperature: Upto 45 degree celsius Life of RO Membrane: Minimum 03 years Pressure Vessels: As per required Pressure Rating: Upto 17 Barg
9 | Automatic PLC Panel
Origin: Europe / USA / German or Equivalent Programming: Fully automatic with breaker, timer and relays complete in all respects HMI display: For PLC - 10" minimum size with touch screen (Fully automatic control of plant) SCADA enable
10 | Anti Scalent + Injection System
Origin: Europe / USA / German or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade Material: PVDF
11 | UV Light with SS casing
Origin: Europe / USA / German or Equivalent Material of Casing: SS 304 / 316 Operating Pressure: 04 Barg Ambient Temperature: Upto 45 degree celsius
12 | Raw & Product water tank (1000 L) Each
Material: PE Food Grade
13 | Level Meter / Float Valve / Switch Electronic
No: 02 Origin: Europe / USA / German or Equiavlent
14 | Water Flow Meter
No: 02 Origin: Europe / USA / German or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic
15 | Pressure Gauges
16 | Online TDS meter
17 | All fittings of PVC Sch.80
18 | Pressure Regulation Switch
19 | Auto on/off Switch for Pump
20 | Automatic Back Wash system for Membrane
21 | Including any item required for Filtration Plant if required
Total |  |  |  | 2129660
Assistant Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority

## B4 R2 New (hidden)
PUNJAB SAAF PANI AUTHORITY
LAHORE DISTRICT
ENGINEERING COST ESTIMATE
Bill No 4 : Installation of Reverse Osmosis 2000 LPH
RO 2000 LPH Plant
Sr No | Description | Qty | Unit Rate (Rs) | Amount (Rs)
1 | Supply, transport, erection, installation, testing & commissioning of 2,000 L/H Reverse Osmosis (RO) Plant for TDS removal along with all other contaminants, including carriage, loading/unloading charges inclusive of all taxes conforming to Mentioned in Technical specifications of filtration plants. Control PLC GSM/GPRS/ SCADA enabled. The unit should be composed of Raw and Product water tanks (2000Liter capacity for each) Feed and High Pressure Pump, pressure gauges, variable area flow meter for raw water and for product water totalizer/ water meter, pressure safety switch and valves, Multiport valves, safety filter strainers/cartridges filter, sand filter, carbon filters. System should be fully automatic. Provission of UV system, Anti secalent system with Anti secalent PVDF based dosing Pumps and chemical tank. The complete plant should be able to operate/backwash automatically through Automatic Multiport Valve operated by PLC with same feed pump based system. All type of piping and instrumentation shall be considered as part of filtration plant complete in all respect. The plant should be supplied to provide the treated water as per the WHO limits (strict compliance). The specifications along with equipment and accessories properly mounted in the frame/skid are given below: | 1 | 2831355 | 2831355
2 | Raw Water Feed Pump
Discharge: 4000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / German / Pakistan or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: SS 304 Discharge: As per the capacity of Plant (4000 LPH) Operating Head: Up to 06 Barg Pump Efficiency: >60% Motor Starter: Star Delta
3 | Submersible Pump
Discharge: 4000 LPH Minimum Operation Head: Up to 130 m. Origin: Europe / USA / German / Pakistan or Equivalent Pump Type: Submersible Pump Impeller Type: SS 304 Discharge: As per the capacity of Plant (4000 LPH) Pump Efficiency: >60% Motor Starter: Star Delta
4 | Pre-Filtration
4 (a) | Sand Filter
Material: FRP Origin: Europe / USA / German or Equivalent Fitration Rate: 6 - 15 m/hr Vessel Certification: NSF Operating Pressure Max: Up to 06 Barg
4 (b) | Filter Media Sand
Material: Quartz Silica Sand Origin: Europe / USA / German or Equivalent Size of Media: 0.6 - 0.8 mm Cleaning Process: Automatic, through PLC / Time Controller MPV
4 (c) | Activated Carbon Filter
Material: FRP Origin: Europe / USA / German or Equivalent Media & Vessel Certification: NSF Fitration Rate: 5 - 15 m/hr Operating Pressure Max: Up to 06 Barg
4 (d) | Filter Media Carbon
Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
4 (e) | Cartridge Filter
Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE
5 | RO Skid
Frame: Stainless Steel
6 | High Pressure Pump multistage
Discharge: 4000 LPH Operating Head: Upto 06 Barg Pump Type: Vertical High Pressure Pump Origin: Europe / USA / German or Equivalent Impeller material: S.S. 304 Pump Efficiency: >60% Motor Starter: Star Delta Motor Temperature Class: 45 degree Celsius Make: Lewara / Grundfous / KSB / CNP / Vilo or Equivalent
7 | RO Housing
Material: FRP Certification: NSF
8 | RO Membrane
Origin: Europe / USA / German or Equivalent (Assembly of Parts may be Pakistan) No. of Stages: Up to 4 No. of Membranes: Up to 8 Certification: NSF Stable salt rejection: Minimum - 99% Capacity: 2000 LPH For Permeate water Capable for TDS: Upto 5000 mg/l Recovery: Should be More than 50% Ambient Temperature: Upto 45 degree celsius Life of RO Membrane: Minimum 03 years Pressure Vessels: As per required Pressure Rating: Upto 17 Barg
9 | Automatic PLC Panel
Origin: Europe / USA / German or Equivalent Programming: Fully automatic with breaker, timer and relays complete in all respects HMI display: For PLC - 10" minimum size with touch screen (Fully automatic control of plant) SCADA enable
10 | Anti Scalent + Injection System
Origin: Europe / USA / German or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade Material: PVDF
11 | UV Light with SS casing
Origin: Europe / USA / German or Equivalent Material of Casing: SS 304 / 316 Operating Pressure: 04 Barg Ambient Temperature: Upto 45 degree celsius
12 | Raw & Product water tank (2000 L) Each
Material: PE Food Grade
13 | Level Meter / Float Valve / Switch Electronic
No: 02 Origin: Europe / USA / German or Equiavlent
14 | Water Flow Meter
No: 02 Origin: Europe / USA / German or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic
15 | Pressure Gauges
16 | Online TDS meter
17 | All fittings of PVC Sch.80
18 | Pressure Regulation Switch
19 | Auto on/off Switch for Pump
20 | Automatic Back Wash system for Membrane
21 | Including any item required for Filtration Plant if required
Total |  |  |  | 2831355
Assistant Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority

## B5 U2 New (hidden)
PUNJAB SAAF PANI AUTHORITY
LAHORE DISTRICT
ENGINEERING COST ESTIMATE
Bill No 5 : Installation of Ultra Filtration 2000 LPH
Specification of UF 2000 LPH Plants
Sr No | Description | Specifications | Qty | Unit Rate (Rs) | Amount (Rs)
| Supply, Install, Testing and Commissioning of water Ultra filtration plant, capable of removing Turbidity, Arsenic, Bacteria & Viruses, having capacity of 2000 litres/ hour and fully automated (Auto filtration, flush and backwash process) complete in all respects. Pressure Gauges, Flow Meters and Level Sensors, Multiport and Solenoid Valves, Stainles Steel 304 Frame, All Pipe work including feed water pipe line connection to the delivery pipeline and necessary gate and flow regulating valves, water taps including pipework & uPVC pipe to drain off the spent/ waste water. |  | 1 | 2634290 | 2634290
1 | Pre Filtration
Pressure Sand filtration
| Constant flow valve for fitration backwash | 3way automatic valve with automatic back wash system
| Sand effective size | 0.85 - 2 mm
| Vessel Material | Material FRP, Make Pentair / Frotec / G Fiber or Equivalent NSF certified company
| Vessel diameter / height | size 16" x 65" / Size 24" x 72"
2 | Activited Carbon filtration
| Carbon Media | Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
| Vessel Material | Material FRP, Make Pentair / Frotec / G Fiber or Equivalent NSF certified company
| Vessel diameter / height | size 16" x 65" / Size 24" x 72"
3 | Arscenic Removal Filter
| Arsenic Media | Grannular Ferric Hydroxide oxidation capacity of As3 to As5, Operating Pressure: 1.5 - 3 Bar Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV
| Vessel Material | Material FRP, Make Pentair / Frotec / G Fiber or Equivalent NSF certified company
| Vessel diameter / height | size 16" x 65" / Size 24" x 72"
4 | UF Unit
| Mounting / Frame | Frame stainless steel SS 304
| Pre treatment objectives turbidity | < 1 NTU
5 | Well pump or / with feed pump | Stainless Steel, NEMA Insulation Class F and Pump Efficiency > 50%
6 | UF Membrane
| Membrane Type | Material of vessel: uPVC Removal Size: 0.02 Micron Manufacturer Type: Mutibore (seven bore) Manufecturer: GE Power (IMT) / INGE or Equivalent Filter vessel: uPVC Thickness: 5mm Membrane material: PES (Polystyrene) Country Made: Europe / USA / Germany or Equivalent. Membrane Working pressure: 5 Bar Max Membrane Life: 5 years Bacterail Removal Effciency of UF membrane: 99.9999% log 6 Viruses Removal effciency of the UF membrane: 99.99% log 4 Auto Back wash Working pressure: 0-2 Bar Working temprature: Max 40 degree Celsius
| Trans membrane Pressure (TMP) | <10 bar
| Piping for Units | All fittings of UPVC Sch.80
7 | Dosing Pump | Operational / rinsing
| Dosing Pump working pressure | 5 - 7 bar
| Chemical Used | Anti Scalant Food Grade
| Pre Treatment | Disinfection by UV radiation
| Bacteria | Below Detection level
8 | Control System | Automatic PLC Panel / Micro processor based embedded system
Programming fully automatic with breaker, timer and relays complete in all respects
Visual Display Unit with Membrane Keypad / HMI with Touch interface
Fully automatic control of plant
SCADA enable
9 | Raw water tank | Raw water tank
Capacity 2000 Litre minimum
Material Plastic food grade
Float Switch
10 | Clean Water Storage Tank | Product water tank
Material Plastic food grade
Capacity 2000 Litre minimum
Float Switch
11 | Waste disposal | Discharge in the sanitory sewerage system
Total |  |  |  |  | 2634290
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  | Punjab Aab-e-Pak Authority

## Bill no 3 RO 1000 New (hidden)
PUNJAB SAAF PANI AUTHORITY
LAHORE DISTRICT
ENGINEER'S COST ESTIMATE
Bill No 3 : Installation of Reverse Osmosis 1 m3/hr
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | Supply installation and commissioning of 1000 L/H Reverse Osmosis (RO) Plant for TDS removal up to 5000 mg/l and inclusive of all taxes conforming to standard specifications according to the Punjab Aab-e-Pak Authority. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | No. | 1 | 1929660 | 1929660
| Total Capital |  |  |  | 1929660
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  | Punjab Aab-e-Pak Authority

## Bill No 4 RO 2000 New (hidden)
PUNJAB SAAF PANI AUTHORITY
LAHORE DISTRICT
ENGINEER'S COST ESTIMATE
Bill No 4 : Installation of Reverse Osmosis 2 m3/hr
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | Supply installation and commissioning of 2000 L/H Reverse Osmosis (RO) Plant for TDS removal up to 5000 mg/l and inclusive of all taxes conforming to standard specifications according to the Punjab Aab-e-Pak Authority. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | No. | 1 | 2631355 | 2631355
| Total Capital |  |  |  | 2631355
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  | Punjab Aab-e-Pak Authority

## Bill No 5 UF 2000 New (hidden)
PUNJAB SAAF PANI AUTHORITY
LAHORE DISTRICT
ENGINEER'S COST ESTIMATE
Bill No 5 : Installation of Ultra Filtration 2 m3/hr
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | Supply installation and commissioning of 2000 L/H Ultra Filtration (UF) Plant for removal of Bacteriological & other contaminants and inclusive of all taxes conforming to standard specifications of filtration plants. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | No. | 1 | 2534290 | 2534290
| Total Capital |  |  |  | 2534290
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  | Punjab Aab-e-Pak Authority

## NEW MF 2000 (hidden)
REHABILITATION OF WATER FILTRATION PLANTS IN DISTRICT BAHAWALPUR
INSTALATION OF MF 2000 LPH WFP
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | #REF! | No. | 1 | 637375 | 637375
| Total Capital |  |  |  | 637375
| PRA 5% |  |  |  | 31868.75
| Grand Total :- |  |  |  | 669243.75

## U2
PUNJAB SAAF PANI AUTHORITY | [6 empty] | 39402793 | UF | 3
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD | [6 empty] | 0 | Abnd
BILL OF QUANTITY | [7 empty] | Dys
Bill No. 5: Rehabilitation of Ultra Filtration 2000 LPH | [7 empty] | fun
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR) |  |  | #REF!
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Frame stainless steel | Per Plant | 3 |  |  | 10800
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | Per Plant | 2 |  |  | 19000
3 | N.S | Supply, Installation & Commissioning of UF membrane including membrane housing complete in all respect Origin: Europe / USA or Equivalent. Removal Size: 0.02 Micron Certification: NSF Material of vessel: uPVC Thickness: 5mm Membrane material: PVDF (Polyvinylidene flouride)/ PES (Polyethersulfone) - Multibore technology Membrane Working pressure: upto 5 Bar Membrane Life: Minimum 5 years Bacterail Removal effciency of UF membrane: 99.9999% log 6 Viruses Removal effciency of UF membrane: 99.99% log 4 Auto Backwash enabled Working temprature: Max 40 degree Celsius | Per Plant | 1 |  |  | 608140 | 45000
4 | N.S | Supply Installation and commissioning of 2000 LPH Feed Pump for 2000 LPH UF WFP, complete in all respect Origin: Europe / USA / Asia or Equivalent Discharge: 2000 LPH Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 05 Barg Pump Efficiency: > 40% Motor Starter: DOL | No. | 1 |  |  | 94745 | 80000
5 | N.S | Rehabilitation of UF Feed water pump 4000 LPH, for 2000 LPH UF Plant, complete in all respect | p/job | 2 |  |  | 18800
6 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL | p/job | 3 |  |  | 91365
7 | N.S | Supply and installation of S.S safety filter strainer | p/job | 3 |  |  | 8405
8 | N.S | Supply Installation and Testing of Pressure Switches complete with all respects | p/job | 3 |  |  | 6375
9 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 3 |  |  | 5117
10 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 9 |  |  | 3400
11 | N.S | Supply Installation and testing of Analogue Water meter, complete in all respect | p/job | 1 |  |  | 17540
12 | N.S | Rehabilitation of Analogue Water meter including callibration, complete in all respect | p/job | 2 |  |  | 6000
13 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 6 |  |  | 8500 | 65
14 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 6 |  |  | 3200 | 8
15 | N.S | Supply Installation & Commissioning of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 3 |  |  | 40930
16 | N.S | Rehabilitation of 3way Automatic Multiport Valve, top & bottom distributers, complete in all respect | p/job | 3 |  |  | 8400
17 | N.S | Supply, installation and Testing of Chlorine Dosing Pump with working pressure 5 - 7 Bar imported, along with 80 liter capacity tank with all repects.complete in all respect Origin: Europe / USA / Asia or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Material: PVDF | p/job | 1 |  |  | 89235
18 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 3 |  |  | 45575
19 | N.S | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | p/job | 3 |  |  | 2500
20 | N.S | Supply and installation of 2 No. electric float switch for Water Storage Tank, complete in all respect | No. | 3 |  |  | 3625
21 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 90 |  |  | 1510
22 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 336 |  |  | 70
23 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel Media | kg | 288 |  |  | 70
24 | N.S | Replacement of Granular Feric Hydroxide use for drinking water treatment with oxidation capacity of As3 to As5, commissioning complete in all respect Operating Pressure: 1.5 - 3 Bar Media: Grannular Ferric Hydroxide Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 192 |  |  | 2510
25 | N.S | Supply installation and commissioning of UV lamp rod with quartz complete in all respect Origin: Europe / USA / German or Equivalent | No. | 1
26 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | Per Plant | 2 |  |  | 22000
27 | N.S | Supply installation & testing of Plastic water Taps with fusion joint, complete in all respect | p/job | 15 |  |  | 585
28 | N.S | Rehabilitation of Plant control panel with PLC & HMI complete in all respect | Per Plant | 2 |  |  | 46000
29 | N.S | Supply & Installation of FRP Vessel (Size16 X 65) Origin: Europe / USA / German / China or Equivalent | No. | 1
Grand Total | [6 empty] | #REF!
Per Unit Cost = Grand Total / 3

## U1
PUNJAB SAAF PANI AUTHORITY | [7 empty] | UF | 7
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No. 6: Rehabilitation of Ultra Filtration 1000 LPH
Sr. No. | MRS Ref. # | Description | Unit | Qty. | Unit Rate (PKR) | Amount (PKR)
1 | N.S | Rehabilitation of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation Frame: Frame stainless steel | p/job | 7 |  |  |  |  | 30%
2 | N.S | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | p/job | 4 |  |  |  |  | 30%
3 | N.S | Supply, Installation & Commissioning of UF membrane including membrane housing complete in all respect Origin: Europe / USA or Equivalent. Removal Size: 0.02 Micron Certification: NSF Material of vessel: uPVC Thickness: 5mm Membrane material: PVDF (Polyvinylidene flouride)/ PES (Polyethersulfone) - Multibore technology Membrane Working pressure: upto 5 Bar Membrane Life: Minimum 5 years Bacterail Removal effciency of UF membrane: 99.9999% log 6 Viruses Removal effciency of UF membrane: 99.99% log 4 Auto Backwash enabled Working temprature: Max 40 degree Celsius | Per Plant | 3 |  |  |  |  | 5%
4 | N.S | Supply Installation and commissioning of 1000 LPH Feed Pump for 1000 LPH UF WFP, complete in all respect Origin: Europe / USA / Asia or Equivalent Discharge: 1000 LPH Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 05 Barg Pump Efficiency: > 40% Motor Starter: DOL | No. | 3 |  |  |  |  | 10%
5 | N.S | Rehabilitation of UF Feed water pump 2000 LPH, for 1000 LPH UF Plant, complete in all respect | p/job | 4 |  |  |  |  | 30%
6 | N.S | Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL | p/job | 7 |  |  |  |  | 10%
7 | N.S | Supply and installation of SS safety filter strainer | p/job | 7 |  |  |  |  | 100%
8 | N.S | Supply Installation and Testing of Pressure Switchs complete with all respects | p/job | 7 |  |  |  |  | 40%
9 | N.S | Supply Installation and testing of Rota meter complete in all respect Origin: Europe / USA / German / Pakistan or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic | p/job | 14 |  |  |  |  | 60%
10 | N.S | Supply Installation and Testing of pressure gauges, complete in all respect | p/job | 21 |  |  |  |  | 200%
11 | N.S | Supply Installation and testing of analogue Water meter, complete in all respect | p/job | 4 |  |  |  |  | 20%
12 | N.S | Rehabilitation of analogue water meter including callibration, complete in all respect | p/job | 3 |  |  |  |  | 50%
13 | N.S | Supply Installation and Testing of Solinoid valve complete in all respect | p/job | 14 |  |  |  |  | 50%
14 | N.S | Rehabilitation of Solinoid valve complete in all respect | p/job | 14 |  |  |  |  | 100%
15 | N.S | Supply Installation & Commissioning of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 7 |  |  |  |  | 10%
16 | N.S | Rehabilitation of 3way Multiport Valve, top & bottom distributers, complete in all respect | p/job | 10.5 |  |  |  |  | 60%
17 | N.S | Supply, installation and Testing of Chemical Dosing Pump / Liquid Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank complete in all respect Origin: Europe / USA / Asia or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade | p/job | 5
18 | N.S | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, 3 to 5 mm wall thickness, weight minimum 32 kg, complete in all respects Capacity : 2000 Litre minimum Material: Plastic food grade | p/job | 7
19 | N.S | Chemical Cleaning & repair of Water Storage tanks, complete in all respects at site | p/job | 7
20 | N.S | Supply and installation of 2 No. float switch for Water Storage Tank, complete in all respect | kg | 7 |  |  |  |  | 30%
21 | N.S | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm | kg | 168 |  |  |  |  | 50
22 | N.S | Replacement of Silica sand media supply, installation and commissioning complete in all respect Material: Quartz Silica Sand Size of Media: 0.85 - 2 mm Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 637 |  |  |  |  | 160
23 | N.S | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect Material: Gravel media | kg | 546 |  |  |  |  | 160
24 | N.S | Replacement of Granular Feric Hydroxide use for drinking water treatment with oxidation capacity of As3 to As5, commissioning complete in all respect Operating Pressure: 1.5 - 3 Bar Media: Grannular Ferric Hydroxide Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV | kg | 378
25 | N.S | Supply installation and commissioning of UV lamp rod with quartz complete in all respect Origin: Europe / USA / German or Equivalent | p/job | 5 |  |  |  |  | 100%
26 | N.S | Rehabilitation of Pipe and fittings, complete plant fitting in all respect | no. | 5 |  |  |  |  | 50%
27 | N.S | Supply installation & testing of Plastic water Taps with fussion joint, complete in all respect | p/job | 35 |  |  |  |  | 5
28 | N.S | Rehabilitation of Plant control panel with PLC & HMI complete in all respect | p/job | 5 |  |  |  |  | 100%
29 | N.S | Supply & Installation of FRP Vessel (Size16 X 65) Origin: Europe / USA / German / China or Equivalent | No. | 1
Grand Total | [6 empty] | 0
Per Unit Cost = Grand Total / 7

## R5 N
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 8 : Installation of Reverse Osmosis 500 LPH
RO 500 LPH Plant
Sr. No | Description | Qty | Unit Rate (Rs) | Amount (Rs)
1 | Supply, transport, erection, installation, testing & commissioning of 500 L/H Reverse Osmosis (RO) Plant for TDS removal along with all other contaminants, including carriage, loading/unloading charges inclusive of all taxes conforming to Mentioned in Technical specifications of filtration plants. Control PLC GSM/GPRS/ SCADA enabled. The unit should be composed of Raw and Product water tanks (1000 Liter capacity for each) Feed and High Pressure Pump, pressure gauges, variable area flow meter for raw water and for product water totalizer/ water meter, pressure safety switch and valves, Multiport valves, safety filter strainers/cartridges filter, sand filter, carbon filters. System should be fully automatic. Provission of UV system, Anti secalent system with Anti scalent PVDF based dosing Pumps and chemical tank. The complete plant should be able to operate/backwash automatically through Automatic Multiport Valve operated by PLC with same feed pump based system. All type of piping and instrumentation shall be considered as part of filtration plant complete in all respect. The plant should be supplied to provide the treated water as per the WHO limits (strict compliance). The specifications along with equipment and accessories properly mounted in the frame/skid are given below: | 1
2 | Raw Water Feed Pump
Supply Installation and commissioning of 1000 LPH Feed Pump for 500 LPH RO WFP, complete in all respect Discharge: 1000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / China or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 06 Barg Pump Efficiency: ≥ 40% Motor Starter: DOL
3 | Submersible Pump
Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL
4 | Pre-Filtration
4 (a) | Sand Filter
Material: FRP Origin: Europe / USA / German or Equivalent Fitration Rate: 6 - 15 m/hr Vessel Certification: NSF Operating Pressure Max: Up to 06 Barg
4 (b) | Filter Media Sand
Material: Quartz Silica Sand Origin: Europe / USA / German or Equivalent Size of Media: 0.6 - 0.8 mm Cleaning Process: Automatic, through PLC / Time Controller MPV
4 (c) | Activated Carbon Filter
Material: FRP Origin: Europe / USA / German or Equivalent Media & Vessel Certification: NSF Fitration Rate: 5 - 15 m/hr Operating Pressure Max: Up to 06 Barg
4 (d) | Filter Media Carbon
Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
4 (e) | Cartridge Filter
Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE
5 | RO Skid
Frame: Stainless Steel
6 | High Pressure Pump multistage
Supply, Installation and commissioning of 2000 LPH High Pressure Pump for 1000 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 2000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius
7 | RO Housing
Material: FRP Certification: NSF
8 | RO Membrane
Supply Installation and commissioning of RO Plant membrane (4x40), including Membrane Housing complete in all respect. Origin: Europe / USA or Equivalent Certification: NSF Pore Size: 0.001 Micron Stablized salt rejection: 99% Capable for TDS: Upto 5000 mg/l Recovery: 15% (each) Life of RO Membrane: 03 to 05 years Pressure Rating: Upto 17 Barg
9 | Automatic PLC Panel
Origin: Europe / USA / German or Equivalent Programming: Fully automatic with breaker, timer and relays complete in all respects HMI display: For PLC - 10" minimum size with touch screen (Fully automatic control of plant) SCADA enable
10 | Anti Scalent + Injection System
Origin: Europe / USA / German or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade Material: PVDF
11 | UV Light with SS casing
Origin: Europe / USA / German or Equivalent Material of Casing: SS 304 / 316 Operating Pressure: 04 Barg Ambient Temperature: Upto 45 degree celsius
12 | Raw & Product water tank (1000 L) Each
Material: PE Food Grade
13 | Level Meter / Float Valve / Switch Electronic
No: 02 Origin: Europe / USA / German or Equiavlent
14 | Water Flow Meter
No: 02 Origin: Europe / USA / German or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic
15 | Pressure Gauges
16 | Online TDS meter
17 | All fittings of PVC Sch.80
18 | Pressure Regulation Switch
19 | Auto on/off Switch for Pump
20 | Automatic Back Wash system for Membrane
21 | Including any item required for Filtration Plant if required
Total

## U2 N
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 7 : Installation of Ultra Filtration 2000 LPH
Specification of UF 2000 LPH Plants
Sr No | Description | Specifications | Qty | Unit Rate (Rs) | Amount (Rs)
| Supply, Install, Testing and Commissioning of water Ultra filtration plant, capable of removing Turbidity, Arsenic, Bacteria & Viruses, having capacity of 2000 litres/ hour and fully automated (Auto filtration, flush and backwash process) complete in all respects. Pressure Gauges, Flow Meters and Level Sensors, Multiport and Solenoid Valves, Stainles Steel 304 Frame, All Pipe work including feed water pipe line connection to the delivery pipeline and necessary gate and flow regulating valves, water taps including pipework & uPVC pipe to drain off the spent/ waste water. |  | 1
1 | Pre Filtration
Pressure Sand filtration
| Constant flow valve for fitration backwash | 3way automatic valve with automatic back wash system
| Sand effective size | 0.85 - 2 mm
| Vessel Material | Material FRP, Make Pentair / Frotec / G Fiber or Equivalent NSF certified company
| Vessel diameter / height | size 16" x 65" / Size 24" x 72"
2 | Activited Carbon filtration
| Carbon Media | Iodine No 850-1000 Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
| Vessel Material | Material FRP, Make Pentair / Frotec / G Fiber or Equivalent NSF certified company
| Vessel diameter / height | size 16" x 65" / Size 24" x 72"
3 | Arscenic Removal Filter
| Arsenic Media | Grannular Ferric Hydroxide oxidation capacity of As3 to As5, Operating Pressure: 1.5 - 3 Bar Origin: Europe / USA / German or Equivalent (NSF Certified) Cleaning Process: Automatic, through PLC / Time Controller MPV
| Vessel Material | Material FRP, Make Pentair / Frotec / G Fiber or Equivalent NSF certified company
| Vessel diameter / height | size 16" x 65" / Size 24" x 72"
4 | UF Unit
| Mounting / Frame | Frame stainless steel SS 304
| Pre treatment objectives turbidity | < 1 NTU
5 | Well pump or / with feed pump | Stainless Steel, NEMA Insulation Class F and Pump Efficiency > 50%
6 | UF Membrane
| Membrane Type | Supply, Installation & Commissioning of UF membrane including membrane housing complete in all respect Origin: Europe / USA or Equivalent. Removal Size: 0.02 Micron Certification: NSF Material of vessel: uPVC Thickness: 5mm Membrane material: PVDF (Polyvinylidene flouride)/ PES (Polyethersulfone) - Multibore technology Membrane Working pressure: upto 5 Bar Membrane Life: Minimum 5 years Bacterail Removal effciency of UF membrane: 99.9999% log 6 Viruses Removal effciency of UF membrane: 99.99% log 4 Auto Backwash enabled Working temprature: Max 40 degree Celsius
| Trans membrane Pressure (TMP) | <10 bar
| Piping for Units | All fittings of UPVC Sch.80
7 | Dosing Pump | Operational / rinsing
| Dosing Pump working pressure | 5 - 7 bar
| Chemical Used | Anti Scalant Food Grade
| Pre Treatment | Disinfection by UV radiation
| Bacteria | Below Detection level
8 | Control System | Automatic PLC Panel / Micro processor based embedded system
Programming fully automatic with breaker, timer and relays complete in all respects
Visual Display Unit with Membrane Keypad / HMI with Touch interface
Fully automatic control of plant
SCADA enable
9 | Raw water tank | Raw water tank
Capacity 2000 Litre minimum
Material Plastic food grade
Float Switch
10 | Clean Water Storage Tank | Product water tank
Material Plastic food grade
Capacity 2000 Litre minimum
Float Switch
11 | Waste disposal | Discharge in the sanitory sewerage system
Total

## R2 N
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 9 : Installation of Reverse Osmosis 2000 LPH
RO 2000 LPH Plant
Sr No | Description | Qty | Unit Rate (Rs) | Amount (Rs)
1 | Supply, transport, erection, installation, testing & commissioning of 2,000 L/H Reverse Osmosis (RO) Plant for TDS removal along with all other contaminants, including carriage, loading/unloading charges inclusive of all taxes conforming to Mentioned in Technical specifications of filtration plants. Control PLC GSM/GPRS/ SCADA enabled. The unit should be composed of Raw and Product water tanks (2000Liter capacity for each) Feed and High Pressure Pump, pressure gauges, variable area flow meter for raw water and for product water totalizer/ water meter, pressure safety switch and valves, Multiport valves, safety filter strainers/cartridges filter, sand filter, carbon filters. System should be fully automatic. Provission of UV system, Anti secalent system with Anti secalent PVDF based dosing Pumps and chemical tank. The complete plant should be able to operate/backwash automatically through Automatic Multiport Valve operated by PLC with same feed pump based system. All type of piping and instrumentation shall be considered as part of filtration plant complete in all respect. The plant should be supplied to provide the treated water as per the WHO limits (strict compliance). The specifications along with equipment and accessories properly mounted in the frame/skid are given below: | 1
2 | Raw Water Feed Pump
Supply Installation and commissioning of 4000 LPH Feed Pump for 2000 LPH RO WFP, complete in all respect Discharge: 4000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / China or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 06 Barg Pump Efficiency: ≥ 40% Motor Starter: DOL
3 | Submersible Pump
Supply Installation & commissioning of submersible pump 3HP including supporting clamp with steel cable, pump coupling, cable clip, delivery pipe, electric cable complete in all respect. Origin: Europe / USA/ Asia or Equivalent Minimum Discharge: 2000 LPH Minimum Operation Head: Up to 130 m. Pump Type: Submersible Pump Impeller Type: S.S. 304 Motor Starter: DOL
4 | Pre-Filtration
4 (a) | Sand Filter
Material: FRP Origin: Europe / USA / German or Equivalent Fitration Rate: 6 - 15 m/hr Vessel Certification: NSF Operating Pressure Max: Up to 06 Barg
4 (b) | Filter Media Sand
Material: Quartz Silica Sand Origin: Europe / USA / German or Equivalent Size of Media: 0.6 - 0.8 mm Cleaning Process: Automatic, through PLC / Time Controller MPV
4 (c) | Activated Carbon Filter
Material: FRP Origin: Europe / USA / German or Equivalent Media & Vessel Certification: NSF Fitration Rate: 5 - 15 m/hr Operating Pressure Max: Up to 06 Barg
4 (d) | Filter Media Carbon
Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
4 (e) | Cartridge Filter
Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE
5 | RO Skid
Frame: Stainless Steel
6 | High Pressure Pump multistage
Supply, Installation and commissioning of 4000 LPH High Pressure Pump for 2000 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 4000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius
7 | RO Housing
Material: FRP Certification: NSF
8 | RO Membrane
Supply Installation and commissioning of RO Plant membrane (4x40), including Membrane Housing complete in all respect. Origin: Europe / USA or Equivalent Certification: NSF Pore Size: 0.001 Micron Stablized salt rejection: 99% Capable for TDS: Upto 5000 mg/l Recovery: 15% (each) Life of RO Membrane: 03 to 05 years Pressure Rating: Upto 17 Barg
9 | Automatic PLC Panel
Origin: Europe / USA / German or Equivalent Programming: Fully automatic with breaker, timer and relays complete in all respects HMI display: For PLC - 10" minimum size with touch screen (Fully automatic control of plant) SCADA enable
10 | Anti Scalent + Injection System
Origin: Europe / USA / German or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade Material: PVDF
11 | UV Light with SS casing
Origin: Europe / USA / German or Equivalent Material of Casing: SS 304 / 316 Operating Pressure: 04 Barg Ambient Temperature: Upto 45 degree celsius
12 | Raw & Product water tank (2000 L) Each
Material: PE Food Grade
13 | Level Meter / Float Valve / Switch Electronic
No: 02 Origin: Europe / USA / German or Equiavlent
14 | Water Flow Meter
No: 02 Origin: Europe / USA / German or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic
15 | Pressure Gauges
16 | Online TDS meter
17 | All fittings of PVC Sch.80
18 | Pressure Regulation Switch
19 | Auto on/off Switch for Pump
20 | Automatic Back Wash system for Membrane
21 | Including any item required for Filtration Plant if required
Total

## R1 N
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 10 : Installation of Reverse Osmosis 1000 LPH
RO 1000 LPH Plant
Sr. No | Description | Qty | Unit Rate (Rs) | Amount (Rs)
1 | Supply, transport, erection, installation, testing & commissioning of 1,000 L/H Reverse Osmosis (RO) Plant for TDS removal along with all other contaminants, including carriage, loading/unloading charges inclusive of all taxes conforming to Mentioned in Technical specifications of filtration plants. Control PLC GSM/GPRS/ SCADA enabled. The unit should be composed of Raw and Product water tanks (1000 Liter capacity for each) Feed and High Pressure Pump, pressure gauges, variable area flow meter for raw water and for product water totalizer/ water meter, pressure safety switch and valves, Multiport valves, safety filter strainers/cartridges filter, sand filter, carbon filters. System should be fully automatic. Provission of UV system, Anti secalent system with Anti scalent PVDF based dosing Pumps and chemical tank. The complete plant should be able to operate/backwash automatically through Automatic Multiport Valve operated by PLC with same feed pump based system. All type of piping and instrumentation shall be considered as part of filtration plant complete in all respect. The plant should be supplied to provide the treated water as per the WHO limits (strict compliance). The specifications along with equipment and accessories properly mounted in the frame/skid are given below: | 1
2 | Raw Water Feed Pump
Supply Installation and commissioning of 2000 LPH Feed Pump for 1000 LPH RO WFP, complete in all respect Discharge: 2000 LPH Minimum Operation Head: 04 Barg Maximum. Origin: Europe / USA / China or Equivalent Pump Type: Vertical / Horizontal Low Pressure Pump Impeller Type: S.S. 304 Operating Head: Up to 06 Barg Pump Efficiency: ≥ 40% Motor Starter: DOL
3 | Submersible Pump
Supply, Installation and commissioning of 2000 LPH High Pressure Pump for 1000 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 2000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius
4 | Pre-Filtration
4 (a) | Sand Filter
Material: FRP Origin: Europe / USA / German or Equivalent Fitration Rate: 6 - 15 m/hr Vessel Certification: NSF Operating Pressure Max: Up to 06 Barg
4 (b) | Filter Media Sand
Material: Quartz Silica Sand Origin: Europe / USA / German or Equivalent Size of Media: 0.6 - 0.8 mm Cleaning Process: Automatic, through PLC / Time Controller MPV
4 (c) | Activated Carbon Filter
Material: FRP Origin: Europe / USA / German or Equivalent Media & Vessel Certification: NSF Fitration Rate: 5 - 15 m/hr Operating Pressure Max: Up to 06 Barg
4 (d) | Filter Media Carbon
Material: Coconut Shell Origin: Sri Lanka / Thailand or Equivalent Size of Media: 1.2 - 1.6 mm Surface Area: 900 m2 / g Bulk Density: 440 - 540 kg / m3 Hardness No: 80 Ash Contents: 5 % Height of Gravel: 200 mm Media Bed Height: > 800 mm
4 (e) | Cartridge Filter
Size: 20 Inches / As per Flow Porosity: 1-5 micron Material: High pressure Plastic Melt Blown PE
5 | RO Skid
Frame: Stainless Steel
6 | High Pressure Pump multistage
Supply, Installation and commissioning of 2000 LPH High Pressure Pump for 1000 LPH RO WFP, complete in all respect Origin: Europe / USA / Japan or Equivalent Discharge: 2000 LPH Operating Head: Up to 16 Barg Pump Type: Vertical / Horizontal High Pressure Pump Impeller material: S.S. 304 Pump Efficiency: > 50% Motor Starter: DOL IP 55 Ambient Temperature Class: 45 degree Celsius
7 | RO Housing
Material: FRP Certification: NSF
8 | RO Membrane
Supply Installation and commissioning of RO Plant membrane (4x40), including Membrane Housing complete in all respect. Origin: Europe / USA or Equivalent Certification: NSF Pore Size: 0.001 Micron Stablized salt rejection: 99% Capable for TDS: Upto 5000 mg/l Recovery: 15% (each) Life of RO Membrane: 03 to 05 years Pressure Rating: Upto 17 Barg
9 | Automatic PLC Panel
Origin: Europe / USA / German or Equivalent Programming: Fully automatic with breaker, timer and relays complete in all respects HMI display: For PLC - 10" minimum size with touch screen (Fully automatic control of plant) SCADA enable
10 | Anti Scalent + Injection System
Origin: Europe / USA / German or Equivalent Pressure: 5 -7 bar Tank Size: Maximum 80 liter Chemical Anti Sclanet: Food Grade Material: PVDF
11 | UV Light with SS casing
Origin: Europe / USA / German or Equivalent Material of Casing: SS 304 / 316 Operating Pressure: 04 Barg Ambient Temperature: Upto 45 degree celsius
12 | Raw & Product water tank (1000 L) Each
Material: PE Food Grade
13 | Level Meter / Float Valve / Switch Electronic
No: 02 Origin: Europe / USA / German or Equiavlent
14 | Water Flow Meter
No: 02 Origin: Europe / USA / German or Equiavlent Type: Rota Meter / Flow Type Material: Acryclic
15 | Pressure Gauges
16 | Online TDS meter
17 | All fittings of PVC Sch.80
18 | Pressure Regulation Switch
19 | Auto on/off Switch for Pump
20 | Automatic Back Wash system for Membrane
21 | Including any item required for Filtration Plant if required
Total

## BH
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 11: Installation of New Bore Holes
Sr. No. | MRS | Description | Unit | Qty | Rate | Total Amount (Rs)
1 | N.S | Boring of tubewell with 350 ft dept, along with casing Pipe (PVC Class B - 4" i/d), discharge Pipe (PVC class B - 1.5" i/d) with steel wire, copper cable for connection of motor, M.S clamp, strainer (B.S.S. Class 'B' - 4" i/d) , Bail/End Plug (4"), reinforced cement concrete in retaining/Shear walls, with contructing of foundation (3'*3'*3'), control panel, etc complete in all respect. | Job | 1
|  |  | M | 30
1 | 23-2-b | Boring for tubewell in all types of soil except shingle, gravel & rock, from a depth of 100 ft to 200 ft (30 m to 60m) below ground level, including sinking and withdrawing of casing pipe, complete:- 6"( 150mm)
|  |  | M | 30
30
3 | 6-5-f | Cement concrete plain including placing, compacting, finishing and curing complete (including screening and washing of stone aggregate): Ratio 1: 2: 4
|  |  | Cu.m | 0.5
4 | 6-6-a ii b(i) | (a)(ii)Reinforced cement concrete in retaining/Shear walls laid in situ or precasted in position,or pre stressed members cast ins itu(Formwork on both sides) , complete in all respects: Type C (nominal mix 1:2:4) Upto 9" thick (Avg)
|  |  | Cu.m | 1.5
5 | 23-15-iii | Providing and installing P.V.C. Bail/End plug, in tubewell bore hole:- (4" dia). (100 mm)
|  |  | Each | 1
6 | 23-11-b | Providing and installing, P.V.C. strainer B.S.S. Class 'B' in tubewell bore hole, including sockets and solvents, etc. complete . 4" dia (100mm).
|  |  | per M | 15
7 | 23-17-b | Providing and installing P.V.C. blind pipe, B.S.S. Class `B', in tubewell bore hole, including sockets and solvents and jointing with strainer, etc. complete (4" dia)
|  |  | M | 75
8 | N.S | Providing, fixing, jointing and testing Polypropylene Random Copolymer (PPRC) PN20 pressure pipe for cold and hot water as per DIN 8077-8078, PN 20 for pipes and DIN 16962, PN 25 for fittings (polyfusion welded joints) inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, cutting and making good the chases and holes, complete in all respects.
|  |  | M | 10
9 | N.S | Supply & installation of 1/2" i/d thick M.S Cap for 6" housing pipe joint by means of welding & hinges with lock & locking arrangements.
|  |  | Each | 1
2 | N.S | Taking of water samples (2 bottles each) at the end of the pumping test. Full chemical and bacteriological analysis, of water samples according to WHO. | Each | 1
Total

## WB
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 12:Development of Bore Holes
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | Rehabilitation, Cleaning & Washing existing bore holes by using air compresseor or any other equipment | No. | 1
Total

## B8 Civil (hidden)
PUNJAB SAAF PANI AUTHORITY
ENGINEERING COST ESTIMATE
Civil Room 12*12
Bill No 8: Rehabilitation of Civil Works
SCHEDULE ITEMS BASED ON MRS, 2nd BI-ANNUAL PERIOD (1st Jun, 2024 TO 30th Dec, 2024) Lahore
Sr. | DESCRIPTION | [8 empty] | QTY | UNIT | RATE | AMOUNT
No. | [11 empty] | ( In Rupees)
Chapter. 7 Item No. 5 (i)
1 | Pacca brick work in ground floor:- cement, sand mortar:-Ratio 1:5
| L.W |  | 2 | 13.5 | 0.75 | 10 | = | 203
| S.W |  | 2 | 12 | 0.75 | 10 | = | 180
| Parapet L.W |  | 2 | 16.5 | 0.75 | 1.5 | = | 37
| Parapet S.W |  | 2 | 12 | 0.375 | 1.5 | = | 14
[5 empty] | Total: |  |  | 434 |  | 30 | cft | 419.888 | 12596.64
Chapter. 11 Item No. 9 b,
2 | Cement plaster 1 : 4 upto 20 ft. height
(b) 1/2 inch thick
| Inside |  | 2 | 12 | + | 12 | 10 | = | 480
| under roof |  | 1 | x | 12 | x | 15 | = | 180
| Below plinth |  | 4 | x | 12 | x | 1.25 | = | 60
| D/d | [5 empty] | Total | (Sft) | 720
|  |  | 1 | x | 5 | x | 7 | = | 35
|  |  | 1 | x | 4 | x | 4 | = | 16
[7 empty] | Total | (Sft) | 51
| Net |  | 720 | - | 51 |  |  | = | 669 | 30 | Sft. | 47.082 | 14
Chapter. 6 Item No. 5.f
3 | Cement concrete plain including placing, compacting, finishing and curing complete (including screening and washing of stone aggregate):
| 1 | 12 | x | 12 | x | 0.33 | = | 48 | Sft.
| 1 | 12 | x | 3 | x | 2 | = | 72 | Sft.
Plinth
| 2 | 19.5 | x | 3 | x | 0.33 | = | 39 | Sft.
| 2 | 13.5 | x | 3 | x | 0.33 | = | 27 | Sft.
[7 empty] | Total | 186 | Sft. | 30 | Sft. | 503.778 | 15113.34
Chapter. 4 Item No. 19(a)
4 | Dismantling of plain cement concrete (1:4:8) | [8 empty] | 40 | cft | 82.764 | 3310.56
Chapter. 1 Item No. 1
5 | Carriage of 100 Cft. (2.83 cu.m) of all materials like stone aggregate, spawl, kankar lime (unslaked), surkhi, etc. or 150 Cft. (4.25 cu.m) of timber, by truck or by any other means owned by the contractor. Upto 200 km
| Upto 0 to 10 K.M distance | [5 empty] | = | 1155.5802
| 10.01 to 200 K.M |  |  | 190 | x | 60.8 | = | 11552
[6 empty] | Total | = | 12707.5802 |  |  |  |  | 12707.5802
6 | Repair and Maintenance of panelled doors and windows in all aspects | [11 empty] | 8227
Chapter. 11 Item No. 23 (b ii)
7 | Distempering on new surface. Three Coats
| Walls 2 side | 2 | 4 | 12 | x | 10 | = | 960 | Sft.
| Ceiling |  | 1 | 12 | x | 15 | = | 180 | Sft.
[6 empty] | Total: |  | 1140 | Sft.
| Net: |  | 1140 | - | 51 | = | 1089 | Sft. |  | 1089 | %Sq.ft. | 15.9775 | 174
Chapter. 10 Item No. 46 A(i)
8 | Providing and laying superb quality Porcelain glazed tiles of Master brand, skirting/dado of specified size, Color and Shade with adhesive/ bond over 1/2"thick (1:2) cement plaster i/c the cost of and sealer for finishing the joints, cutting grinding complete in all respect as approved and directed by the Engineer Incharge.
Area
| 1 | x | 12 | x | 12 | = | 144 | Sft.
| 1 | x | 12 | x | 5 | = | 60 | Sft.
[6 empty] | Total: | 204 | Sft. |  | 50 | P Sft. | 386.35 | 19318
CIVIL ROOM | [11 empty] | Total :- | 71461.1203
Assistant Manager (P&MC) - CZ | [7 empty] | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority | [7 empty] | Punjab Aab-e-Pak Authority

## IW
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 13: Injection Well
Sr. No. | MRS | Description | Unit | Qty | Rate | Total Amount (Rs)
1 | N.S | Boring of tubewell with 350 ft dept, along with casing Pipe (PVC Class B - 4" i/d), discharge Pipe (PVC class B - 1.5" i/d), reinforced cement concrete in retaining/Shear walls and etc complete in all respect | Job | 1
Total

## PF F
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No. 14 : Rehabilitation of Pre Fabrication Room
MRS, 1ST BI-ANNUAL-2025 (01.01.2025 to 30.06.2025) FSD
Sr # | Item # | Description | Unit | Quantity | Rate | Amount
[5 empty] | Rs | Rs.
1 | 4/50. | Dismantling glazed or encaustic tiles, etc. | %Sft | 0.9
2 | 7/5-i. | Pacca brick work in ground floor:- i) cement, sand mortar:- Ratio 1:4 | % Cft | 0.2
3 | 11/9-b. | Cement plaster 1:4 upto 20' (6.00 m) height:- b) ½" (13 mm) thick | % Sft | 0.71
4 | 10/24-i. | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size, Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. i) 12"x18"/12"x24"/10"x24"/8"x24" /12"x36" | Sft | 222.25
5 | 10/25-i. | Providing and laying superb quality Ceramic dado floors of Master/Stile brand or approved equivalent manufacturer of specified size, Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. i) 12"x18"/12"x24"/10"x24"/8"x24" /12"x36" | Sft | 43
6 | 13/4a-i+ii. | Painting old surfaces:- a) Painting corrugated surfaces, patent roofing, etc. with oil Paint. i) first coat ii) two subsequent Coats | %Sft | 25.26
7 | 13/4d-i+ii. | Painting guard bars, gates of iron bars, gratings, railing (including standards, braces etc.) and similar open work: i) first coat ii) two subsequent Coats | %Sft | 16.2
8 | 25/10 +11. | Fabrication of heavy steel work, with angle, tees, flat iron round iron and sheet iron for making trusses, girders, tanks, etc., including cutting, drilling, revitting, handling, assembling and fixing, but excluding erection in position. | %Kgs | 1.96
9 | 19/27-i | Providing and fixing chromium plated bib cock: i) 2 cm (¾") | Each | 7
10 | 26/49-iii | Providing and fixing slip joint sandwich panels composed of two steel layers injected in between with polyurethane foam on existing surface, light weight of specified density and fire resistance grade-B. The steel sheet layers are polyester coated hot dipped galvanized, sandwich sheets panels are painted with reflective, anti dust and durable electrostatic paint from both sides i/c the cost of flashing trims, screws, revits, sealants, tapes etc. complete in all respects as approved and directed by the Engineer Incharge. (iii) 75 mm thick | Sft | 64
11 | 24/3-iii | Supply and erection of PVC pipe for wiring recessed in walls, including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. iii) 25 mm i/d | P.Rft | 40
12 | 24/11-i | Supply and erection of single core PVC insulated copper conductor cables, in prelaid PVC pipe/M.S. conduit/G.I pipe/wooden strip batten/wooden casing an capping/G.I. wire/trenches (rate for cables only): 250/440 volts, PVC insulated: i) 3/0.74 mm (3/0.029") | P.Rft | 70
13 | 24/11-iii | Supply and erection of single core PVC insulated copper conductor cables, in prelaid PVC pipe/M.S. conduit/G.I pipe/wooden strip batten/wooden casing an capping/G.I. wire/trenches (rate for cables only): 250/440 volts, PVC insulated: iii) 7/0.74 mm (7/0.029") | P.Rft | 60
14 | 24/108b-iii | P/FPVC doublelayer Switch kit Face plate with specified switch holes i/c the costof switches/ sockets/ dimmer made of Legrand/ABB/Schenider or approved equvilent manufacturer, screw complete in all respect, as approved and directed by the Engineer Incharge b) One way Gange Switch (Large) iii) 06 Gange | Each | 1
15 | 24/105b-ii | Providing and fixing Pakistan Energy Label NEECA approved Copper winded Exaust Fan i/c the cost of necessary cable and hardware for connection from ceiling rose complete asapproved and directed by Engineer Incharge. ) b)Steel body 18" Sweep | Each | 1
16 | NS | Batten light 18 Watt | Each | 5 |  |  | 2242 | 2914.6
TOTAL

## C FSD
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 15: Rehabilitation of Civil Work
MRS, 1ST BI-ANNUAL-2025 (01.01.2025 to 30.06.2025) DISTRICT FAISLABAD
Sr No. | MRS | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate | Amount (Rs)
[6 empty] | Length | Breadth | Height
1 | 7/5 i | Pacca brick work in ground floor:- Ratio (1:5) | [6 empty] | 1.1286 | Cum
| 7/5 i | Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
Total
2 | 11/9-b | Cement plaster (1:4) upto 20'-0" hight ½" thick | [6 empty] | 57.388 | Sqm
|  | Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
|  | Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  |  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  |  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
Total
3 | 7/37 i | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9" | [6 empty] | 25.9308 | Sqm
|  | Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm
Total
4 | 4-50 | Dismantling glazed or encaustic tiles, etc. | [6 empty] | 20.745 | Sqm
5 | 10-24i | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 12.5126 | Sqm
|  |  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 10-24 i | [5 empty] | Total
6 | 10-25 i | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 8.232 | Sqm
|  |  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
Total
7 | 11/ 22+23-b | Distempering new surface 3coats Quantity as Ceiling, Internal & External Plaster | [6 empty] | 51.8616 | Sqm
|  |  | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
Total
8 | 9/20a | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:- | [6 empty] | 4 | M
|  | Roof | 1 | x | 1 | 4 |  |  | 4
Total
9 | 9/21 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
10 | 9/22 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting. | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
11 | 25/09. | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position. | [6 empty] | 300 | Kg
|  |  | 1 | x | 1 | 300 | Kg |  | 300
Total
12 | 25/32 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre. | [6 empty] | 1.4172 | Sqm
|  |  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
Total
13 | 13/5 d i & ii | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat. | [6 empty] | 20.724 | Sqm
|  | Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
|  | M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
Total
14 | 23/47 a iii & iv | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/Beta or approved equivalent manufacturer, with specified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
|  | PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M
|  | PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M
15 | 23/42 c 7 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17) | [6 empty] | 10 | M
|  |  | 1 | x | 1 | 10 |  |  | 10
Total
16 | 19/27 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6 | Each
[8 empty] | Total | 6 | Each
17 | 19/8-iii Rep | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2 | Each
[8 empty] | Total | 2 | Each
18 | 23/26 b | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer. | [6 empty] | 7 | M
|  |  | 1 | x | 1 | 7 |  |  | 7
Total
19 | 11/31. | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks. | [6 empty] | 25.9308 | Sqm
25.9308
|  | 11/31. | [5 empty] | Total
20 | 26/46-i | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever | [6 empty] | 9 | Sqm
|  |  | 1 | x | 1 | 3 | 3 |  | 9
21 | NS | Branding of PSPA | [6 empty] | 1 | Job
22 | NS | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job
23 | 24/3 ii) & iii) | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | [6 empty] | 41.2 | Ft
|  | ii) 25 mm | [6 empty] | 16.1 | Ft
24 | 24/14-a v) | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | [6 empty] | 23.4 | Ft
25 | 24/11 i), ii), iii) & vi) | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | [6 empty] | 52.4 | Ft
|  | ii) 3/0.036" | [6 empty] | 54.5 | Ft
|  | iii) 7/0.029" | [6 empty] | 35.4 | Ft
|  | vi) 7/0.064" | [6 empty] | 9.8 | Ft
26 | N.S | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | [6 empty] | 2 | No.
27 | 24/44 i) | Supply and erection of button holder (bakelite large size). | [6 empty] | 2 | No.
28 | 24/36(ii) | Supply and erection of switches 5 Amp Piano type | [6 empty] | 4 | No.
29 | N.S | Supply and erection of 2 Pin switch with socket. | [6 empty] | 1 | No.
30 | 24/105a(i) | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | [6 empty] | 1 | No.
TOTAL

## C F (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISLABAD
ENGINEERING COST ESTIMATE
Bill No 15: Rehabilitation of Civil Work
1st BI-Annual 2025 FSD
Item No | Description |  | Nos |  |  | Measurements |  |  | Quantity |  | Rate |  | Amount (Rs)
[6 empty] | Length | Breadth | Height
1
1.01 | Pacca brick work in ground floor:- Ratio (1:5)
| Dispenser Platform |  | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
| 7/5 i | [6 empty] | Total | 1.1286 | Cum | 13455.1 | Cum | 15185.5227
1.02 | Cement plaster (1:4) upto 20'-0" hight ½" thick
| Room Outer Side |  | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
| Dispenser Platform |  | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  |  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  |  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
| 11/9-b | [6 empty] | Total | 57.388 | Sqm | 501.5 | Sqm | 28780.0619
1.03 | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9"
| Back Wall |  | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm |  |  |  | Chp-10/15-e | Providing and laying topping screed of cement concrete 1:2:4 (2" ( 50mm) thick), including surface finishing and dividing in panels
[14 empty] | Chp-11/18-b | Deep struck pointing (1:2), complete as per drawing and specification.
| 7/37 i | [6 empty] | Total | 25.9308 | Sqm | 2813.45 | Sqm | 72955.0093
1.04 | Dismantling glazed or encaustic tiles, etc.
|  |  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  |  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 4-50 | [6 empty] | Total | 20.7446 | Sqm | 372.1 | Sqm | 7719.0805
1.05 | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  |  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
| 10-24 i | [6 empty] | Total | 12.5126 | Sqm | 3375.35 | Sqm | 42234.5394
1.06 | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  |  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 10-25 i | [6 empty] | Total | 8.232 | Sqm | 4150.95 | Sqm | 34170.6204
1.07 | Distempering old surface 3coats
| Quantity as Ceiling, Internal & External Plaster |  | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
| 11/ 22+23-b | [6 empty] | Total | 51.8616 | Sqm | 211 | Sqm | 10942.7976
1.08 | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:-
| Roof |  | 1 | x | 1 | 4 |  |  | 4
| 9/20a | [6 empty] | Total | 4 | M | 1619.5 | M | 6478
1.09 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting
| Roof |  | 1 | x | 2 |  |  |  | 2
| 9/21 | [6 empty] | Total | 2 | Each | 1402.45 | P. No | 2804.9
1.1 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting.
| Roof |  | 1 | x | 2 |  |  |  | 2
| 9/22 | [6 empty] | Total | 2 | Each | 702.65 | P. No | 1405.3
1.11 | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position.
|  |  | 1 | x | 1 | 300 | Kg |  | 300
| 25/09. | [6 empty] | Total | 300 | Kg | 493.85 | Kg | 148155
1.12 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre.
|  |  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
| 25/32 | [6 empty] | Total | 1.4172 | Sqm | 11782.3 | Sqm | 16697.8756
1.13 | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat.
| Grating |  | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
| M.S Fence |  | 2 | x | 2 | 4 | 1 |  | 16
[8 empty] | Total | 20.724 | Sqm | 217.65 | Sqm | 4510.5786
13/5 d i & ii
1.14 | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/ Beta or approved equivalent manufacturer, withs pecified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
| PPRC Pipe 40 mm dia |  | 1 | x | 1 | 15 |  |  | 15 | M | 643.15 | M | 9647.25
| PPRC Pipe 32 mm dia |  | 1 | x | 1 | 10 |  |  | 10 | M | 433.95 | M | 4339.5
23/47 a iii & iv
1.15 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17)
|  |  | 1 | x | 1 | 10 |  |  | 10
[8 empty] | Total | 10 | M | 1112.15 | M | 11121.5
23/42 c 7
1.16 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [7 empty] | 6
| 19/27 | [6 empty] | Total | 6 | Each | 1641.4 | Each | 9848.4
1.17 | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [7 empty] | 2
| 19/8-iii Rep | [6 empty] | Total | 2 | Each | 1479 | Each | 2958
1.18 | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer.
|  |  | 1 | x | 1 | 7 |  |  | 7
| 23/26 b | [6 empty] | Total | 7 | M | 1689.9 | M | 11829.3
1.19 | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks.
25.9308
| 11/31. | [6 empty] | Total | 25.9308 | Sqm | 115.7 | Sqm | 3000.1936
1.2 | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever
|  |  | 1 | x | 1 | 3 | 3 |  | 9
| 26/46-i | [6 empty] | Total | 9 | Sqm | 10448.75 | Sqm | 94038.75
1.2 | Branding of PSPA | [7 empty] | 1 | Job | 10000 | Job | 10000
1.21 | Repair of Doors and Windows along with installation of Neon Lights | [7 empty] | 1 | Job | 15031 | Job | 15031
1.22 | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | [7 empty] | 41.2 | Ft | 114.25 | Ft | 4707.1
| ii) 25 mm | [7 empty] | 16.1 | Ft | 135.85 | Ft | 2187.185
24/3 ii) & iii)
1.23 | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | [7 empty] | 23.4 | Ft | 237.9 | Ft | 5566.86
24/14-a v)
1.24 | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | [7 empty] | 52.4 | Ft | 35.9 | Ft | 1881.16
| ii) 3/0.036" | [7 empty] | 54.5 | Ft | 36.3 | Ft | 1978.35
| iii) 7/0.029" | [7 empty] | 35.4 | Ft | 56.5 | Ft | 2000.1
| vi) 7/0.064" | [7 empty] | 9.8 | Ft | 269 | Ft | 2636.2
24/11 i), ii), iii) & vi)
1.25 | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | [7 empty] | 2 | No. | 50 | No. | 100
1.26 | Supply and erection of button holder (bakelite large size). | [7 empty] | 2 | No. | 79.75 | No. | 159.5
24/44 i)
1.27 | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | Supply and erection of switches 5 Amp Piano type | 4 | No. | 104.05 | No. | 416.2
24/36(ii)
1.28 | Supply and erection of 2 Pin switch with socket. | [7 empty] | 1 | No. | 500 | No. | 500
1.29 | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | [7 empty] | 1 | No. | 5568.1 | No. | 5568.1
24/105a(i)
[12 empty] | TOTAL COST OF WATER TREATMENT PLANT = | 591553.9346
Assistant Manager (P&MC) - CZ | [7 empty] | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority | [7 empty] | Punjab Saaf Pani Authority

## C CHI
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 16: Rehabilitation of Civil Work
MRS, 1ST BI-ANNUAL-2025 (01.01.2025 to 30.06.2025) DISTRICT CHINIOT
Sr No. | MRS | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate | Amount (Rs)
[6 empty] | Length | Breadth | Height
1 | 7/5 i | Pacca brick work in ground floor:- Ratio (1:5) | [6 empty] | 1.1286 | Cum
| 7/5 i | Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
Total
2 | 11/9-b | Cement plaster (1:4) upto 20'-0" hight ½" thick | [6 empty] | 57.388 | Sqm
|  | Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
|  | Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  |  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  |  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
Total
3 | 7/37 i | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9" | [6 empty] | 25.9308 | Sqm
|  | Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm
Total
4 | 4-50 | Dismantling glazed or encaustic tiles, etc. | [6 empty] | 20.745 | Sqm
5 | 10-24i | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 12.5126 | Sqm
|  |  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 10-24 i | [5 empty] | Total
6 | 10-25 i | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 8.232 | Sqm
|  |  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
Total
7 | 11/ 22+23-b | Distempering new surface 3coats Quantity as Ceiling, Internal & External Plaster | [6 empty] | 51.8616 | Sqm
|  |  | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
Total
8 | 9/20a | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:- | [6 empty] | 4 | M
|  | Roof | 1 | x | 1 | 4 |  |  | 4
Total
9 | 9/21 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
10 | 9/22 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting. | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
11 | 25/09. | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position. | [6 empty] | 300 | Kg
|  |  | 1 | x | 1 | 300 | Kg |  | 300
Total
12 | 25/32 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre. | [6 empty] | 1.4172 | Sqm
|  |  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
Total
13 | 13/5 d i & ii | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat. | [6 empty] | 20.724 | Sqm
|  | Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
|  | M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
Total
14 | 23/47 a iii & iv | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/Beta or approved equivalent manufacturer, with specified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
|  | PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M
|  | PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M
15 | 23/42 c 7 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17) | [6 empty] | 10 | M
|  |  | 1 | x | 1 | 10 |  |  | 10
Total
16 | 19/27 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6 | Each
[8 empty] | Total | 6 | Each
17 | 19/8-iii Rep | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2 | Each
[8 empty] | Total | 2 | Each
18 | 23/26 b | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer. | [6 empty] | 7 | M
|  |  | 1 | x | 1 | 7 |  |  | 7
Total
19 | 11/31. | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks. | [6 empty] | 25.9308 | Sqm
25.9308
|  | 11/31. | [5 empty] | Total
20 | 26/46-i | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever | [6 empty] | 9 | Sqm
|  |  | 1 | x | 1 | 3 | 3 |  | 9
21 | NS | Branding of PSPA | [6 empty] | 1 | Job
22 | NS | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job
23 | 24/3 ii) & iii) | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | [6 empty] | 41.2 | Ft
|  | ii) 25 mm | [6 empty] | 16.1 | Ft
24 | 24/14-a v) | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | [6 empty] | 23.4 | Ft
25 | 24/11 i), ii), iii) & vi) | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | [6 empty] | 52.4 | Ft
|  | ii) 3/0.036" | [6 empty] | 54.5 | Ft
|  | iii) 7/0.029" | [6 empty] | 35.4 | Ft
|  | vi) 7/0.064" | [6 empty] | 9.8 | Ft
26 | N.S | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | [6 empty] | 2 | No.
27 | 24/44 i) | Supply and erection of button holder (bakelite large size). | [6 empty] | 2 | No.
28 | 24/36(ii) | Supply and erection of switches 5 Amp Piano type | [6 empty] | 4 | No.
29 | N.S | Supply and erection of 2 Pin switch with socket. | [6 empty] | 1 | No.
30 | 24/105a(i) | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | [6 empty] | 1 | No.
TOTAL

## C JHA
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 17: Rehabilitation of Civil Work
MRS, 1ST BI-ANNUAL-2025 (01.01.2025 to 30.06.2025) DISTRICT JHANG
Sr No. | MRS | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate | Amount (Rs)
[6 empty] | Length | Breadth | Height
1 | 7/5 i | Pacca brick work in ground floor:- Ratio (1:5) | [6 empty] | 1.1286 | Cum
| 7/5 i | Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
Total
2 | 11/9-b | Cement plaster (1:4) upto 20'-0" hight ½" thick | [6 empty] | 57.388 | Sqm
|  | Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
|  | Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  |  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  |  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
Total
3 | 7/37 i | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9" | [6 empty] | 25.9308 | Sqm
|  | Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm
Total
4 | 4-50 | Dismantling glazed or encaustic tiles, etc. | [6 empty] | 20.745 | Sqm
5 | 10-24i | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 12.5126 | Sqm
|  |  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 10-24 i | [5 empty] | Total
6 | 10-25 i | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 8.232 | Sqm
|  |  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
Total
7 | 11/ 22+23-b | Distempering new surface 3coats Quantity as Ceiling, Internal & External Plaster | [6 empty] | 51.8616 | Sqm
|  |  | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
Total
8 | 9/20a | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:- | [6 empty] | 4 | M
|  | Roof | 1 | x | 1 | 4 |  |  | 4
Total
9 | 9/21 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
10 | 9/22 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting. | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
11 | 25/09. | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position. | [6 empty] | 300 | Kg
|  |  | 1 | x | 1 | 300 | Kg |  | 300
Total
12 | 25/32 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre. | [6 empty] | 1.4172 | Sqm
|  |  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
Total
13 | 13/5 d i & ii | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat. | [6 empty] | 20.724 | Sqm
|  | Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
|  | M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
Total
14 | 23/47 a iii & iv | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/Beta or approved equivalent manufacturer, with specified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
|  | PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M
|  | PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M
15 | 23/42 c 7 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17) | [6 empty] | 10 | M
|  |  | 1 | x | 1 | 10 |  |  | 10
Total
16 | 19/27 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6 | Each
[8 empty] | Total | 6 | Each
17 | 19/8-iii Rep | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2 | Each
[8 empty] | Total | 2 | Each
18 | 23/26 b | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer. | [6 empty] | 7 | M
|  |  | 1 | x | 1 | 7 |  |  | 7
Total
19 | 11/31. | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks. | [6 empty] | 25.9308 | Sqm
25.9308
|  | 11/31. | [5 empty] | Total
20 | 26/46-i | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever | [6 empty] | 9 | Sqm
|  |  | 1 | x | 1 | 3 | 3 |  | 9
21 | NS | Branding of PSPA | [6 empty] | 1 | Job
22 | NS | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job
23 | 24/3 ii) & iii) | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | [6 empty] | 41.2 | Ft
|  | ii) 25 mm | [6 empty] | 16.1 | Ft
24 | 24/14-a v) | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | [6 empty] | 23.4 | Ft
25 | 24/11 i), ii), iii) & vi) | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | [6 empty] | 52.4 | Ft
|  | ii) 3/0.036" | [6 empty] | 54.5 | Ft
|  | iii) 7/0.029" | [6 empty] | 35.4 | Ft
|  | vi) 7/0.064" | [6 empty] | 9.8 | Ft
26 | N.S | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | [6 empty] | 2 | No.
27 | 24/44 i) | Supply and erection of button holder (bakelite large size). | [6 empty] | 2 | No.
28 | 24/36(ii) | Supply and erection of switches 5 Amp Piano type | [6 empty] | 4 | No.
29 | N.S | Supply and erection of 2 Pin switch with socket. | [6 empty] | 1 | No.
30 | 24/105a(i) | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | [6 empty] | 1 | No.
TOTAL

## C TTS
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 18: Rehabilitation of Civil Work
MRS, 1ST BI-ANNUAL-2025 (01.01.2025 to 30.06.2025) DISTRICT TOBA TEK SINGH
Sr No. | MRS | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate | Amount (Rs)
[6 empty] | Length | Breadth | Height
1 | 7/5 i | Pacca brick work in ground floor:- Ratio (1:5) | [6 empty] | 1.1286 | Cum
| 7/5 i | Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
Total
2 | 11/9-b | Cement plaster (1:4) upto 20'-0" hight ½" thick | [6 empty] | 57.388 | Sqm
|  | Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
|  | Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  |  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  |  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
Total
3 | 7/37 i | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9" | [6 empty] | 25.9308 | Sqm
|  | Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm
Total
4 | 4-50 | Dismantling glazed or encaustic tiles, etc. | [6 empty] | 20.745 | Sqm
5 | 10-24i | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 12.5126 | Sqm
|  |  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 10-24 i | [5 empty] | Total
6 | 10-25 i | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge. | [6 empty] | 8.232 | Sqm
|  |  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
Total
7 | 11/ 22+23-b | Distempering new surface 3coats Quantity as Ceiling, Internal & External Plaster | [6 empty] | 51.8616 | Sqm
|  |  | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
Total
8 | 9/20a | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:- | [6 empty] | 4 | M
|  | Roof | 1 | x | 1 | 4 |  |  | 4
Total
9 | 9/21 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
10 | 9/22 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting. | [6 empty] | 2 | Each
|  | Roof | 1 | x | 2 |  |  |  | 2
Total
11 | 25/09. | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position. | [6 empty] | 300 | Kg
|  |  | 1 | x | 1 | 300 | Kg |  | 300
Total
12 | 25/32 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre. | [6 empty] | 1.4172 | Sqm
|  |  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
Total
13 | 13/5 d i & ii | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat. | [6 empty] | 20.724 | Sqm
|  | Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
|  | M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
Total
14 | 23/47 a iii & iv | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/Beta or approved equivalent manufacturer, with specified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
|  | PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M
|  | PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M
15 | 23/42 c 7 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17) | [6 empty] | 10 | M
|  |  | 1 | x | 1 | 10 |  |  | 10
Total
16 | 19/27 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6 | Each
[8 empty] | Total | 6 | Each
17 | 19/8-iii Rep | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2 | Each
[8 empty] | Total | 2 | Each
18 | 23/26 b | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer. | [6 empty] | 7 | M
|  |  | 1 | x | 1 | 7 |  |  | 7
Total
19 | 11/31. | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks. | [6 empty] | 25.9308 | Sqm
25.9308
|  | 11/31. | [5 empty] | Total
20 | 26/46-i | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever | [6 empty] | 9 | Sqm
|  |  | 1 | x | 1 | 3 | 3 |  | 9
21 | NS | Branding of PSPA | [6 empty] | 1 | Job
22 | NS | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job
23 | 24/3 ii) & iii) | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | [6 empty] | 41.2 | Ft
|  | ii) 25 mm | [6 empty] | 16.1 | Ft
24 | 24/14-a v) | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | [6 empty] | 23.4 | Ft
25 | 24/11 i), ii), iii) & vi) | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | [6 empty] | 52.4 | Ft
|  | ii) 3/0.036" | [6 empty] | 54.5 | Ft
|  | iii) 7/0.029" | [6 empty] | 35.4 | Ft
|  | vi) 7/0.064" | [6 empty] | 9.8 | Ft
26 | N.S | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | [6 empty] | 2 | No.
27 | 24/44 i) | Supply and erection of button holder (bakelite large size). | [6 empty] | 2 | No.
28 | 24/36(ii) | Supply and erection of switches 5 Amp Piano type | [6 empty] | 4 | No.
29 | N.S | Supply and erection of 2 Pin switch with socket. | [6 empty] | 1 | No.
30 | 24/105a(i) | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | [6 empty] | 1 | No.
TOTAL

## C C (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATE
Bill No 16: Rehabilitation of Civil Work
1st BI-Annual 2025 CHINIOT
Item No | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate |  | Amount (Rs)
[5 empty] | Length | Breadth | Height
1
1.01 | Pacca brick work in ground floor:- Ratio (1:5)
| Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
| 7/5 i | [5 empty] | Total | 1.1286 | Cum | 12458.9 | Cum | 14061.2042
1.02 | Cement plaster (1:4) upto 20'-0" hight ½" thick
| Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
| Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
| 11/9-b | [5 empty] | Total | 57.388 | Sqm | 496.95 | Sqm | 28518.9467
1.03 | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9"
| Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm |  |  |  | Chp-10/15-e | Providing and laying topping screed of cement concrete 1:2:4 (2" ( 50mm) thick), including surface finishing and dividing in panels
[13 empty] | Chp-11/18-b | Deep struck pointing (1:2), complete as per drawing and specification.
| 7/37 i | [5 empty] | Total | 25.9308 | Sqm | 2796.8 | Sqm | 72523.2614
1.04 | Dismantling glazed or encaustic tiles, etc.
|  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 4-50 | [5 empty] | Total | 20.7446 | Sqm | 366.45 | Sqm | 7601.8733
1.05 | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
| 10-24 i | [5 empty] | Total | 12.5126 | Sqm | 3363.95 | Sqm | 42091.8953
1.06 | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 10-25 i | [5 empty] | Total | 8.232 | Sqm | 4139.6 | Sqm | 34077.1872
1.07 | Distempering old surface 3coats
| Quantity as Ceiling, Internal & External Plaster | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
| 11/ 22+23-b | [5 empty] | Total | 51.8616 | Sqm | 138.55 | Sqm | 7185.4247
1.08 | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:-
| Roof | 1 | x | 1 | 4 |  |  | 4
| 9/20a | [5 empty] | Total | 4 | M | 1612.3 | M | 6449.2
1.09 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting
| Roof | 1 | x | 2 |  |  |  | 2
| 9/21 | [5 empty] | Total | 2 | Each | 1390.6 | P. No | 2781.2
1.1 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting.
| Roof | 1 | x | 2 |  |  |  | 2
| 9/22 | [5 empty] | Total | 2 | Each | 699.35 | P. No | 1398.7
1.11 | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position.
|  | 1 | x | 1 | 300 | Kg |  | 300
| 25/09. | [5 empty] | Total | 300 | Kg | 492.2 | Kg | 147660
1.12 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre.
|  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
| 25/32 | [5 empty] | Total | 1.4172 | Sqm | 11756.55 | Sqm | 16661.3827
1.13 | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat.
| Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
| M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
[7 empty] | Total | 20.724 | Sqm | 215.2 | Sqm | 4459.8048
13/5 d i & ii
1.14 | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/ Beta or approved equivalent manufacturer, withs pecified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
| PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M | 642.8 | M | 9642
| PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M | 433.6 | M | 4336
23/47 a iii & iv
1.15 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17)
|  | 1 | x | 1 | 10 |  |  | 10
[7 empty] | Total | 10 | M | 1111.95 | M | 11119.5
23/42 c 7
1.16 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6
| 19/27 | [5 empty] | Total | 6 | Each | 1639.2 | Each | 9835.2
1.17 | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2
| 19/8-iii Rep | [5 empty] | Total | 2 | Each | 1479 | Each | 2958
1.18 | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer.
|  | 1 | x | 1 | 7 |  |  | 7
| 23/26 b | [5 empty] | Total | 7 | M | 1688.85 | M | 11821.95
1.19 | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks.
25.9308
| 11/31. | [5 empty] | Total | 25.9308 | Sqm | 113.95 | Sqm | 2954.8147
1.2 | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever
|  | 1 | x | 1 | 3 | 3 |  | 9
| 26/46-i | [5 empty] | Total | 9 | Sqm | 10440.5 | Sqm | 93964.5
1.2 | Branding of PSPA | [6 empty] | 1 | Job | 10000 | Job | 10000
1.21 | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job | 15031 | Job | 15031
[11 empty] | TOTAL COST OF WATER TREATMENT PLANT = | 557133.0451
Assistant Manager (P&MC) - CZ | [6 empty] | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority | [6 empty] | Punjab Saaf Pani Authority

## C J (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATE
Bill No 17: Rehabilitation of Civil Work
1st BI-Annual 2025 JHANG
Item No | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate |  | Amount (Rs)
[5 empty] | Length | Breadth | Height
1
1.01 | Pacca brick work in ground floor:- Ratio (1:5)
| Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
| 7/5 i | [5 empty] | Total | 1.1286 | Cum | 12534.8 | Cum | 14146.8655
1.02 | Cement plaster (1:4) upto 20'-0" hight ½" thick
| Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
| Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
| 11/9-b | [5 empty] | Total | 57.388 | Sqm | 496.95 | Sqm | 28518.9467
1.03 | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9"
| Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm |  |  |  | Chp-10/15-e | Providing and laying topping screed of cement concrete 1:2:4 (2" ( 50mm) thick), including surface finishing and dividing in panels
[13 empty] | Chp-11/18-b | Deep struck pointing (1:2), complete as per drawing and specification.
| 7/37 i | [5 empty] | Total | 25.9308 | Sqm | 2796.8 | Sqm | 72523.2614
1.04 | Dismantling glazed or encaustic tiles, etc.
|  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 4-50 | [5 empty] | Total | 20.7446 | Sqm | 366.45 | Sqm | 7601.8733
1.05 | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
| 10-24 i | [5 empty] | Total | 12.5126 | Sqm | 3363.95 | Sqm | 42091.8953
1.06 | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 10-25 i | [5 empty] | Total | 8.232 | Sqm | 4139.6 | Sqm | 34077.1872
1.07 | Distempering old surface 3coats
| Quantity as Ceiling, Internal & External Plaster | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
| 11/ 22+23-b | [5 empty] | Total | 51.8616 | Sqm | 208.9 | Sqm | 10833.8882
1.08 | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:-
| Roof | 1 | x | 1 | 4 |  |  | 4
| 9/20a | [5 empty] | Total | 4 | M | 1612.3 | M | 6449.2
1.09 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting
| Roof | 1 | x | 2 |  |  |  | 2
| 9/21 | [5 empty] | Total | 2 | Each | 1390.6 | P. No | 2781.2
1.1 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting.
| Roof | 1 | x | 2 |  |  |  | 2
| 9/22 | [5 empty] | Total | 2 | Each | 699.35 | P. No | 1398.7
1.11 | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position.
|  | 1 | x | 1 | 300 | Kg |  | 300
| 25/09. | [5 empty] | Total | 300 | Kg | 492.12 | Kg | 147636
1.12 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre.
|  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
| 25/32 | [5 empty] | Total | 1.4172 | Sqm | 11756.55 | Sqm | 16661.3827
1.13 | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat.
| Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
| M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
[7 empty] | Total | 20.724 | Sqm | 215.02 | Sqm | 4456.0745
13/5 d i & ii
1.14 | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/ Beta or approved equivalent manufacturer, withs pecified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
| PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M | 642.8 | M | 9642
| PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M | 433.6 | M | 4336
23/47 a iii & iv
1.15 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17)
|  | 1 | x | 1 | 10 |  |  | 10
[7 empty] | Total | 10 | M | 1111.95 | M | 11119.5
23/42 c 7
1.16 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6
| 19/27 | [5 empty] | Total | 6 | Each | 1639.2 | Each | 9835.2
1.17 | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2
| 19/8-iii Rep | [5 empty] | Total | 2 | Each | 1479 | Each | 2958
1.18 | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer.
|  | 1 | x | 1 | 7 |  |  | 7
| 23/26 b | [5 empty] | Total | 7 | M | 1688.85 | M | 11821.95
1.19 | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks.
25.9308
| 11/31. | [5 empty] | Total | 25.9308 | Sqm | 113.95 | Sqm | 2954.8147
1.2 | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever
|  | 1 | x | 1 | 3 | 3 |  | 9
| 26/46-i | [5 empty] | Total | 9 | Sqm | 10440.5 | Sqm | 93964.5
1.2 | Branding of PSPA | [6 empty] | 1 | Job | 10000 | Job | 10000
1.21 | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job | 15031 | Job | 15031
[11 empty] | TOTAL COST OF WATER TREATMENT PLANT = | 560839.4396
Assistant Manager (P&MC) - CZ | [6 empty] | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority | [6 empty] | Punjab Saaf Pani Authority

## C T (hidden)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATE
Bill No 18: Rehabilitation of Civil Work
1st BI-Annual 2025 TTS
Item No | Description | Nos |  |  | Measurements |  |  | Quantity |  | Rate |  | Amount (Rs)
[5 empty] | Length | Breadth | Height
1
1.01 | Pacca brick work in ground floor:- Ratio (1:5)
| Dispenser Platform | 1 | x | 1 | 4.116 | 0.914 | 0.3 | 1.1286 | Cum
| 7/5 i | [5 empty] | Total | 1.1286 | Cum | 13455.1 | Cum | 15185.5227
1.02 | Cement plaster (1:4) upto 20'-0" hight ½" thick
| Room Outer Side | 1 | x | 4 | 4.116 |  | 3.15 | 51.8616 | Sqm
| Dispenser Platform | 1 | x | 1 | 4.116 |  | 0.91 | 3.7456 | Sqm
|  | 1 | x | 1 | 4.116 |  | 0.3 | 1.2348 | Sqm
|  | 1 | x | 2 | 0.91 |  | 0.3 | 0.546 | Sqm
| 11/9-b | [5 empty] | Total | 57.388 | Sqm | 501.5 | Sqm | 28780.0619
1.03 | Providing and laying fair face Gutka cladding laid in(1:2)cement / red posso mortar having 1/4" thick groove finishing/c cost of 8SWGwirein shape of 8 placed horizontally and vertically at 36" and 18" c/c respectively i/c cutting charges as per approved drawing, complete in all respect as approved and directed by the Engineer Incharge. i. 2-1/4" x 2-1/4" x 9"
| Back Wall | 0.5 | x | 4 | 4.116 |  | 3.15 | 25.9308 | Sqm |  |  |  | Chp-10/15-e | Providing and laying topping screed of cement concrete 1:2:4 (2" ( 50mm) thick), including surface finishing and dividing in panels
[13 empty] | Chp-11/18-b | Deep struck pointing (1:2), complete as per drawing and specification.
| 7/37 i | [5 empty] | Total | 25.9308 | Sqm | 2813.45 | Sqm | 72955.0093
1.04 | Dismantling glazed or encaustic tiles, etc.
|  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
|  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 4-50 | [5 empty] | Total | 20.7446 | Sqm | 366.45 | Sqm | 7601.8733
1.05 | Providing and laying superb quality Ceramic tile floors of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 3/4" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  | 1 | x | 1 | 4.116 | 3.04 |  | 12.5126 | Sqm
| 10-24 i | [5 empty] | Total | 12.5126 | Sqm | 3375.35 | Sqm | 42234.5394
1.06 | Providing and laying superb quality Ceramic tile dado of Master/Stile brand or approved equivalent manufacturer of specified size,Glossy/Matt/Texture of approved Color and Shade as per approved design with adhesive bond, over 1/2" thick (1;2) cement sand plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects and as approved and directed by the Engineer Incharge.
|  | 1 | x | 1 | 4.116 | 2 |  | 8.232 | Sqm
| 10-25 i | [5 empty] | Total | 8.232 | Sqm | 4150.95 | Sqm | 34170.6204
1.07 | Distempering old surface 3coats
| Quantity as Ceiling, Internal & External Plaster | 1 | x | 1 | 51.8616 |  |  | 51.8616 | Sqm
| 11/ 22+23-b | [5 empty] | Total | 51.8616 | Sqm | 211 | Sqm | 10942.7976
1.08 | Cast iron rain water downpipe fixed in position, excluding heads and shoes, but including painting and clamps, etc:-
| Roof | 1 | x | 1 | 4 |  |  | 4
| 9/20a | [5 empty] | Total | 4 | M | 1619.5 | M | 6478
1.09 | Rain water down pipe cast iron head fixed in place, including cost of clamp holdfast and painting
| Roof | 1 | x | 2 |  |  |  | 2
| 9/21 | [5 empty] | Total | 2 | Each | 1402.45 | P. No | 2804.9
1.1 | Shoes, bends or offsets for cast iron rain water down pipe, including fixing and painting.
| Roof | 1 | x | 2 |  |  |  | 2
| 9/22 | [5 empty] | Total | 2 | Each | 702.65 | P. No | 1405.3
1.11 | Small iron work, such as gusset plates, knees, bends, stirrups, straps, rings, etc. including cutting, drilling, riveting, handling, assembling and fixing; but excluding erection in position.
|  | 1 | x | 1 | 300 | Kg |  | 300
| 25/09. | [5 empty] | Total | 300 | Kg | 493.85 | Kg | 148155
1.12 | Making and fixing grating in opening, including fixing at site with flat iron 2"x3/8" (50x10 mm) and ¾" (19 mm) square bars, at 4" (100 mm) centre to centre.
|  | 1 | x | 1 | 4.724 | 0.3 |  | 1.4172
| 25/32 | [5 empty] | Total | 1.4172 | Sqm | 11782.3 | Sqm | 16697.8756
1.13 | Painting new surface:-Preparing surface and painting guard bars, gates of iron bars, gratings, railing (including standards braces, etc.) and in similar open work Three Coats including priming coat.
| Grating | 1 | x | 2 | 4.724 | 0.5 |  | 4.724
| M.S Fence | 2 | x | 2 | 4 | 1 |  | 16
[7 empty] | Total | 20.724 | Sqm | 217.65 | Sqm | 4510.5786
13/5 d i & ii
1.14 | Providing, laying, testing and commissioning of POLYPROPYLENE RANDOM COPOLYMER (PPRC) water supplypipe(Dadex /Popular/ Beta or approved equivalent manufacturer, withs pecified pressure rating PN (PRESSURENOMINAL) and conforming to DIN8077-8078 code i/c cost of solvent,specials,making jharries complete in all respectas approved and directed by Engineer Incharge. (Internal/External Diameters mentioned). a) PN-16 pipe
| PPRC Pipe 40 mm dia | 1 | x | 1 | 15 |  |  | 15 | M | 643.15 | M | 9647.25
| PPRC Pipe 32 mm dia | 1 | x | 1 | 10 |  |  | 10 | M | 433.95 | M | 4339.5
23/47 a iii & iv
1.15 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE-100) working presure pipe in trenches. complete in all respects:- 3" (90mm) PN-10 (SDR-17)
|  | 1 | x | 1 | 10 |  |  | 10
[7 empty] | Total | 10 | M | 1112.15 | M | 11121.5
23/42 c 7
1.16 | Providing and fixing chromium plated bib cock:- ii) 1.5 cm (1/2"). | [6 empty] | 6
| 19/27 | [5 empty] | Total | 6 | Each | 1641.4 | Each | 9848.4
1.17 | Providing and fixing brass ball float valve:- 2.5 cm (1") dia | [6 empty] | 2
| 19/8-iii Rep | [5 empty] | Total | 2 | Each | 1479 | Each | 2958
1.18 | Providing, laying, cutting, jointing, testing and disinfecting P.V.C. pipe line with `B' Class working pressure pipe, in trenches, complete in all respects 4" i/d (100 mm):- as per drawing, specifications and approval of the Engineer.
|  | 1 | x | 1 | 7 |  |  | 7
| 23/26 b | [5 empty] | Total | 7 | M | 1689.9 | M | 11829.3
1.19 | Extra cost of labour and material for red oxide pigment in cement pointing to match with the colour of bricks.
25.9308
| 11/31. | [5 empty] | Total | 25.9308 | Sqm | 115.7 | Sqm | 3000.1936
1.2 | Supply and Erection of 10 ft high Cantilever type Car Parking Shed consisting of 3mm thick fiber glass sheet roof fixed/ riveted with molded curved frame comprising of 1-1/2"x1-1/2"16-SWG MS box placed @2ft C/C both side sand1-1/2"x3"M.Sbox16-SWG at front and back side welded on cantilever arch type MS pipe 3"dia arms welded with 3/8" thick and 8"dia Main Post duly welded with 1/2" thick 1.5'x1.5' base plate and 4 no stiffeners of 1/2" thick MS sheet embedded in PCC 2'x2'x3'with18" long nut bolts1" dia i/c cost of foundation, cutting straightening assembling, bending as per drawing, welding/grinding of joints and painting three coats complete in all respect as approved by the Engineer Incharge. (i) One side Cantilever
|  | 1 | x | 1 | 3 | 3 |  | 9
| 26/46-i | [5 empty] | Total | 9 | Sqm | 10448.75 | Sqm | 94038.75
1.2 | Branding of PSPA | [6 empty] | 1 | Job | 10000 | Job | 10000
1.21 | Repair of Doors and Windows along with installation of Neon Lights | [6 empty] | 1 | Job | 15031 | Job | 15031
[11 empty] | TOTAL COST OF WATER TREATMENT PLANT = | 563735.9724
Assistant Manager (P&MC) - CZ | [6 empty] | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority | [6 empty] | Punjab Saaf Pani Authority

## B19 PF
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No. 19: Pre Fabricated Room for Plant 12x12
Sr # | Description | Qty | Rate | Total Rs.
6.1 | Prefabricated Room for Plant Supply and installation of Pre-fabricated room size 12 ft x 12 ft + 3ft | 1
Wall panel: Shall constitute of Sandwich panel 75 mm layer medium density polystyrene and 0.45 mm Pre-Painted Formed steel sheet (Prime Quality) with Fire Retardant thermal insulating core of polystyrene 15-16 kg/m3.
Roof Panel: Shall constitute of Sandwich panel 75mm with top 0.45 mm Pre-Painted Trapezoidal Corrugated steel sheet and bottom 0.45 mm Pre-Painted Formed steel sheet (Prime Quality) with thermal insulating core of polystyrene 15-16 kg/m3
Structure: U Channel: 40 x 75 x 1.5mm thick & 60 x 75 x 1.5mm thick C Channel: 50 x 200 x 12 x 1.5mm thick as per approved drawings complete in all respects.
Door: 50mm thick Steel Sandwich Panel Door of the same material as used in walls. 1.5mm G.I Channel door chowkat. Door frame is made of 0.45mm PPGI/Aluminum Channel
Window: 1.5mm thick Silver Color Aluminum Window with 5 mm clear glass (1220mm x 1220mm)
Ventilator: 1.5mm thick Silver Color Aluminum Ventilator with 5mm clear glass.(600mmx400mm)
Drain Channel: 0.45mm Pre-Painted Formed steel sheet.
Rawal Bolt, Roof Drilling Screw, Decorative Covers and Hardware, etc.Manufacturing of all trims, flashing as per approved drawings complete in all respects.
Prefabricated Room (A)
Foundation for Pre Fabricated Room (Sub Head 19 (i)) - (B)
Electrification Works (SubHead 19 (ii)) - (C)
Grand Total for Pre Fabricated Room 12x12 (A+B+C)

## B19(i)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Sub Head 19 (i): Foundation of Pre-Fabricated Room 12 x 12 (1ST Bi Annual Faislabad)
Sr No. | MRS | Description | [7 empty] | Quantity |  | Rate | Amount (Rs)
1 | 3/21-1(ii) | Excavation in foundation of building, bridges and other structures, including dagbelling, dressing, refilling around structure with excavated earth, watering and ramming lead upto one chain (30 m) and lift upto 5 ft. (in ordinary soil). | [7 empty] | 474.1087 | Cft
|  | Room Walls Front, Back & side walls |  | 1 | x | 1 | 51 | 3.125 | 2.21 | 352.2188
|  | Plinth protection for Side walls & Back wall |  | 1 | x | 1 | 51 | 1 | 1.23 | 62.73
|  | Plinth protection for front wall |  | 1 | x | 1 | 51 | 1 | 1.16 | 59.16
Total
2 | 26/44 | Spraying anti termite proofing by using liquid FMC Biflex 2.5%EC Mixing Ratio 1:50=137-Sft or using liquid MIRAGE Ali Akbar /RANGERS Auriga 5% SC Mixing Ability-HEXTAR Ratio 1:110=205-Sft or any other equivalent approved liquid applying with shower and certificate will be provided by the contractor for 10- years complete in all respect .as approved by the Engineer Incharge. | [7 empty] | 225.42 | Sft
|  | Room foundation |  | 1 | x | 2 | 51 | 0 | 2.21 | 225.42 | Sft
Total
3 | 3/5 ii & 17d | Earth Filling in ordinary soil lead up 8 km with compaction upto required 90% modified AATSHO dry density complete in all respects as approved by the Engineer Incharge. | [7 empty] | 18.3937 | Cft
|  | Room |  | 1 | x | 1 | 10.5 | 10.5 | 1.75 | 192.9375
|  | Excavated Soil 60% of Excavated Material |  | -1 | x | 1 | 51 | 3.125 | 2.21 | -211.3312
|  | 3/5 ii & 17d | [6 empty] | Total
4 | 6/2. | Dry rammed brick or stone ballast, 1½" to 2"( 40 mm to 50 mm) gauge. | [7 empty] | 27.5625 | Cft
|  | Room Floor |  | 1 | x | 1 | 10.5 | 10.5 | 0.25 | 27.5625
Total
5 | 6/5(f) | Cement concrete plain including placing, compacting, finishing and curing complete (including screening and washing of stone aggregate): P.C.C (1:2:4) | [7 empty] | 250.23 | Cft
|  | In Room walls foundation |  | 1 | x | 1 | 51 | 3.125 | 0.33 | 52.5938
|  | For Room Floor |  | 1 | x | 1 | 10.5 | 10.5 | 0.33 | 36.3825
|  | In plinth protection foundation |  | 1 | x | 1 | 60.5 | 1 | 0.25 | 15.125
|  | Plinth protection P.C.C of Side and back walls |  | 1 | x | 1 | 47.5 | 2.75 | 0.5 | 65.3125
|  | Plinth protection P.C.C of front walls |  | 1 | x | 1 | 10.5 | 4 | 1.21 | 50.82
|  | Dispensing area |  | 1 | x | 1 | 12 | 2 | 1.25 | 30
|  | 6/5(f) | [6 empty] | Total | 250.2337 | Cft
6 | 10/25 i | Providing and laying superb quality Ceramic tiles dado of Master brand of specified size,Glossy/Matt/Texture skirting/dado of approved Color and Shade with adhesive bond over 1/2"thick (1:2) cement plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects as approved and directed by the Engineer Incharge.i) 12"x18" | [7 empty] | 133.88 | Sft
|  | Room |  | 1 | x | 1 | 10.5 | 12.75 |  | 133.875 | Sft
|  | 10/25 i | [6 empty] | Total | 133.875 | Sft
7 | 7/ 4 i (Page-52) | Pacca brick work in foundation and plinth in:- Ratio (1:5) | [7 empty] | 84.041 | Cft
For Plinth proection of Side and back wall
|  |  | 1st Step | 1 | x | 1 | 53 | 0.75 | 1 | 39.75 | Cft
For Plinth proection of front wall
|  |  | 1st Step | 1 | x | 1 | 10.5 | 0.75 | 0.91 | 7.1663 | Cft
For 6" brick work above plinth
|  |  |  | 1 | x | 1 | 51 | 0.75 | 0.5 | 19.125 | Cft
|  | Dispensing Area brick work |  | 1 | x | 1 | 12 | 3 | 0.5 | 18
|  | 7/ 4 i (Page-52) | [6 empty] | Total | 84.0412 | Cft
8 | 6/6(c) (3) | Reinforced cement concrete in slab of rafts / strip foundation, base slab of column and retaining walls; etc and footing beams, other structural members other than those mentioned in 6(a) (i)&(ii) above not requiring form work (i.e. horizontal shuttering) complete in all respects:- | [7 empty] | 173.145 | Cft
|  | Front, Back and Side wall | Ist Step | 1 | x | 1 | 51 | 2.125 | 0.5 | 54.1875
|  |  | 2nd Step | 1 | x | 1 | 51 | 0.75 | 3.11 | 118.9575
|  | 6/6(c) (3) | [6 empty] | Total | 173.145 | Cft
9 | 6/ 13,ii | Fabrication of mild steel reinforcement for cement concrete, The rate includes wastage, overlaps including cutting, bending, laying in position, making joints and chairs, etc and fastenings, including cost of binding wire and labour charges for binding of steel reinforcement (also includes removal of rust from bars):- | [7 empty] | 125.6 | kg
|  | In foundation |  | 0.35% of foundation Concrete #4 | [5 empty] | 125.6 | kg
|  | 6/ 13,ii | [6 empty] | Total | 125.6 | kg
10 | 6/39 b-ii-b | Providing and laying vertical damp proof course with cement sand plaster and bitumen coating, (b) with 2 coats of bitumen:- (1:3) ¾ " thick | [7 empty] | 58.38 | sft
|  | Room Walls |  | 1 | x | 1 | 42 | 1.39 |  | 58.38 | sft
|  | 6/39 b-ii-b | [6 empty] | Total | 58.38 | sft
1.11 |  | Railing |  |  |  |  | 16.5 |  | 1.5 | 16.5 | ft
11 | NS | Railing | [7 empty] | 16.5 | ft
Total (Sub Head 19 (i)) - (B)

## B19(ii)
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
SubHead 19 (ii): Electrification Work of Water Filtration Plant Room (1ST Bi Annual Faisalabad)
MRS No. | Description | Unit | Qty | Unit Rate | Amount
CH-24/3 ii) & iii) | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | ft | 41.2
| ii) 25 mm | ft | 16.1
CH-24/1-a ii) | Supply and erection of G.I. pipes for wiring purposes, including pull boxes, inspection boxes, bends, tees, etc. complete with all specials (on surface, including clamps, etc.) i) 20 mm | ft | 10.2
CH-24/14-a v) | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | ft | 23.4
CH-24/11 i), ii), iii) & vi) | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | ft | 52.4
| ii) 3/0.036" | ft | 54.5
| iii) 7/0.029" | ft | 35.4
| vi) 7/0.064" | ft | 9.8
NS | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | No. | 2
CH-24/44 i) | Supply and erection of button holder (bakelite large size). | No. | 2
CH-24/36(ii) | Supply and erection of switches 5 Amp Piano type | No. | 4
NS | Supply and erection of 2 Pin switch with socket. | No. | 1
CH-24/48 ii) | Supply and erection of Single rod (40 watts) with one choke and one starter tube light, including rod, choke, starter with frame, flexible wire, including connection from ceiling rose, etc., complete. | Set | 2
NS | Supply, installation and commissioning of bracket fan 12"/14'' of approved quality, nuts, bolts, from recommended manufacturer, complete in all respects. | No. | 1
Ch-24/105a(i) | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | No. | 1
NS | Supply, Installation, testing and commissioning of Earthing set complete with accessories (Rod length should be 3 meter) as per drawings. To achieve Earthing value less than 1 Ohm, complete in all respects as approved by Engineer In charge. | Set | 1
Total (SubHead 19 (ii)) - (C)

## PFR F (hidden)
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATES
Bill No. 19: Pre Fabricated Room for Plant 12x12
Sr # | Description | Qty | Rate | AMOUNT Rs.
6.1 | Prefabricated Room for Plant Supply and installation of Pre-fabricated room size 12 ft x 12 ft + 3ft | 1 | 979155 | 979155
Wall panel: Shall constitute of Sandwich panel 75 mm layer medium density polystyrene and 0.45 mm Pre-Painted Formed steel sheet (Prime Quality) with Fire Retardant thermal insulating core of polystyrene 15-16 kg/m3.
Roof Panel: Shall constitute of Sandwich panel 75mm with top 0.45 mm Pre-Painted Trapezoidal Corrugated steel sheet and bottom 0.45 mm Pre-Painted Formed steel sheet (Prime Quality) with thermal insulating core of polystyrene 15-16 kg/m3
Structure: U Channel: 40 x 75 x 1.5mm thick & 60 x 75 x 1.5mm thick C Channel: 50 x 200 x 12 x 1.5mm thick as per approved drawings complete in all respects.
Door: 50mm thick Steel Sandwich Panel Door of the same material as used in walls. 1.5mm G.I Channel door chowkat. Door frame is made of 0.45mm PPGI/Aluminum Channel
Window: 1.5mm thick Silver Color Aluminum Window with 5 mm clear glass (1220mm x 1220mm)
Ventilator: 1.5mm thick Silver Color Aluminum Ventilator with 5mm clear glass.(600mmx400mm)
Drain Channel: 0.45mm Pre-Painted Formed steel sheet.
Rawal Bolt, Roof Drilling Screw, Decorative Covers and Hardware, etc.Manufacturing of all trims, flashing as per approved drawings complete in all respects.
Prefabricated Room |  |  |  | 979155
Foundation for Pre Fabricated Room |  |  |  | 382427.5582
Electrification Works |  |  |  | 63103.375
Grand Total for Pre Fabricated Room 12x12 |  |  |  | 1424685.9332
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority |  | Punjab Saaf Pani Authority

## B19(i) F (hidden)
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATES
Sub Head 19 (i): Foundation of Pre-Fabricated Room 12 x 12 (1ST Bi Annual FSD)
Item No | Description |  | Nos |  |  | Measurements |  |  | Quantity |  | Rate |  | Amount (Rs)
[6 empty] | Length | Breadth | Height
1
1.01 | Excavation in foundation of building, bridges and other structures, including dagbelling, dressing, refilling around structure with excavated earth, watering and ramming lead upto one chain (30 m) and lift upto 5 ft. (in ordinary soil).
| Room Walls Front, Back & side walls |  | 1 | x | 1 | 51 | 3.125 | 2.21 | 352.2188
| Plinth protection for Side walls & Back wall |  | 1 | x | 1 | 51 | 1 | 1.23 | 62.73
| Plinth protection for front wall |  | 1 | x | 1 | 51 | 1 | 1.16 | 59.16
| 3/21-1(ii) | [6 empty] | Total | 474.1087 | Cft | 15.84 | Cft | 7509.8826
1.02 | Spraying anti termite proofing by using liquid FMC Biflex 2.5%EC Mixing Ratio 1:50=137-Sft or using liquid MIRAGE Ali Akbar /RANGERS Auriga 5% SC Mixing Ability-HEXTAR Ratio 1:110=205-Sft or any other equivalent approved liquid applying with shower and certificate will be provided by the contractor for 10- years complete in all respect .as approved by the Engineer Incharge.
| Room foundation |  | 1 | x | 2 | 51 | 0 | 2.21 | 225.42 | Sft
| 26/44 | [6 empty] | Total | 225.42 | Sft | 12.55 | Sft | 2829.021
1.03 | Earth Filling in ordinary soil lead up 8 km with compaction upto required 90% modified AATSHO dry density complete in all respects as approved by the Engineer Incharge.
| Room |  | 1 | x | 1 | 10.5 | 10.5 | 1.75 | 192.9375
| Excavated Soil 60% of Excavated Material |  | -1 | x | 1 | 51 | 3.125 | 2.21 | -211.3312
| 3/5 ii & 17d | [6 empty] | Total | 18.3937 | Cft | 9.7224 | Cft | 178.8305 | 9597
1.04 | Dry rammed brick or stone ballast, 1½" to 2"( 40 mm to 50 mm) gauge.
| Room Floor |  | 1 | x | 1 | 10.5 | 10.5 | 0.25 | 27.5625
| 6/2. | [6 empty] | Total | 27.5625 | Cft | 123.09 | Cft | 3392.6681
1.05 | Cement concrete plain including placing, compacting, finishing and curing complete (including screening and washing of stone aggregate): P.C.C (1:2:4)
| In Room walls foundation |  | 1 | x | 1 | 51 | 3.125 | 0.33 | 52.5938
| For Room Floor |  | 1 | x | 1 | 10.5 | 10.5 | 0.33 | 36.3825
| In plinth protection foundation |  | 1 | x | 1 | 60.5 | 1 | 0.25 | 15.125
| Plinth protection P.C.C of Side and back walls |  | 1 | x | 1 | 47.5 | 2.75 | 0.5 | 65.3125
| Plinth protection P.C.C of front walls |  | 1 | x | 1 | 10.5 | 4 | 1.21 | 50.82
| Dispensing area |  | 1 | x | 1 | 12 | 2 | 1.25 | 30
| 6/5(f) | [6 empty] | Total | 250.2337 | Cft | 497.97 | Cft | 124608.9005
1.06 | Providing and laying superb quality Ceramic tiles dado of Master brand of specified size,Glossy/Matt/Texture skirting/dado of approved Color and Shade with adhesive bond over 1/2"thick (1:2) cement plaster i/c the cost of sealer for finishing the joints i/c cutting grinding complete in all respects as approved and directed by the Engineer Incharge.i) 12"x18"
| Room |  | 1 | x | 1 | 10.5 | 12.75 |  | 133.875 | Sft
| 10/25 i | [6 empty] | Total | 133.875 | Sft | 385.8 | Sft | 51648.975
1.07 | Pacca brick work in foundation and plinth in:- Ratio (1:5)
For Plinth proection of Side and back wall
|  | 1st Step | 1 | x | 1 | 53 | 0.75 | 1 | 39.75 | Cft
For Plinth proection of front wall
|  | 1st Step | 1 | x | 1 | 10.5 | 0.75 | 0.91 | 7.1663 | Cft
For 6" brick work above plinth
|  |  | 1 | x | 1 | 51 | 0.75 | 0.5 | 19.125 | Cft
| Dispensing Area brick work |  | 1 | x | 1 | 12 | 3 | 0.5 | 18
| 7/ 4 i (Page-52) | [6 empty] | Total | 84.0412 | Cft | 371.42 | Cft | 31214.6011
1.08 | Reinforced cement concrete in slab of rafts / strip foundation, base slab of column and retaining walls; etc and footing beams, other structural members other than those mentioned in 6(a) (i)&(ii) above not requiring form work (i.e. horizontal shuttering) complete in all respects:-
| Front, Back and Side wall | Ist Step | 1 | x | 1 | 51 | 2.125 | 0.5 | 54.1875
|  | 2nd Step | 1 | x | 1 | 51 | 0.75 | 3.11 | 118.9575
| 6/6(c) (3) | [6 empty] | Total | 173.145 | Cft | 622.45 | Cft | 107774.1052
1.09 | Fabrication of mild steel reinforcement for cement concrete, The rate includes wastage, overlaps including cutting, bending, laying in position, making joints and chairs, etc and fastenings, including cost of binding wire and labour charges for binding of steel reinforcement (also includes removal of rust from bars):-
| In foundation |  | 0.35% of foundation Concrete #4 | [5 empty] | 125.6 | kg
| 6/ 13,ii | [6 empty] | Total | 125.6 | kg | 303.38 | Cft | 38104.528
1.1 | Providing and laying vertical damp proof course with cement sand plaster and bitumen coating, (b) with 2 coats of bitumen:- (1:3) ¾ " thick
| Room Walls |  | 1 | x | 1 | 42 | 1.39 |  | 58.38 | sft
| 6/39 b-ii-b | [6 empty] | Total | 58.38 | sft | 88.49 | sft | 5166.0462
1.11 | Railing |  |  |  |  | 16.5 |  | 1.5 | 16.5 | ft | 10000 |  | 10000
TOTAL COST OF WATER TREATMENT PLANT | [12 empty] | 382427.5582
Assistant Manager (P&MC) - CZ | [7 empty] | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority | [7 empty] | Punjab Saaf Pani Authority

## B19(ii) F (hidden)
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
ENGINEERING COST ESTIMATES
SubHead 19 (ii): ELECTRIFICATION WORKS OF WATER FILTERATION PLANT ROOM (1ST Bi Annual FSD)
SR No. | DESCRIPTION | UNIT | QUANTITY | UNIT RATE (Rs) | AMOUNT (Rs)
CH-24/3 ii) & iii) | Supply and erection of PVC pipe for wiring recessed in walls, floors, roofs including inspection boxes, pull boxes, hooks, cutting jharries, and repairing surface, etc., complete with all specials. i) 20 mm | ft | 41.2 | 114.25 | 4707.1
| ii) 25 mm | ft | 16.1 | 135.85 | 2187.185
CH-24/1-a ii) | Supply and erection of G.I. pipes for wiring purposes, including pull boxes, inspection boxes, bends, tees, etc. complete with all specials (on surface, including clamps, etc.) i) 20 mm | ft | 10.2 | 273.1 | 2785.62
CH-24/14-a v) | Supply and erection of PVC insulated, PVC sheathed twin core, 250/440 volts copper conductor cables for service connection, in prelaid pipe/G.I. wire/trenches, etc. (rate for cable only):- i) 7/0.044" | ft | 23.4 | 237.9 | 5566.86
CH-24/11 i), ii), iii) & vi) | Supply and erection of single core PVC insulated, PVC sheathed copper conductor, 250/440 volts grade cable (BSS-2004), in prelaid PVC pipes/M.S. conduit/G.I. pipe/wooden strip batten/wooden casing and capping/trenches, etc. (rate for cable only):- i) 3/0.029" | ft | 52.4 | 35.9 | 1881.16
| ii) 3/0.036" | ft | 54.5 | 36.3 | 1978.35
| iii) 7/0.029" | ft | 35.4 | 56.5 | 2000.1
| vi) 7/0.064" | ft | 9.8 | 269 | 2636.2
NS | Supply and installation of 4" deep u-PVC concealed switch box for recessed wiring, including making holes for regulators, switches, plugs, etc. | No. | 2 | 50 | 100
CH-24/44 i) | Supply and erection of button holder (bakelite large size). | No. | 2 | 79.75 | 159.5
CH-24/36(ii) | Supply and erection of switches 5 Amp Piano type | No. | 4 | 104.05 | 416.2
NS | Supply and erection of 2 Pin switch with socket. | No. | 1 | 500 | 500
CH-24/48 ii) | Supply and erection of Single rod (40 watts) with one choke and one starter tube light, including rod, choke, starter with frame, flexible wire, including connection from ceiling rose, etc., complete. | Set | 2 | 2008.5 | 4017
NS | Supply, installation and commissioning of bracket fan 12"/14'' of approved quality, nuts, bolts, from recommended manufacturer, complete in all respects. | No. | 1 | 3600 | 3600
Ch-24/105a(i) | Providing and fixing Copper winded Exhaust fan with louver and shutter made of Pak/Younas/G.F.C. i/c the cost of necessary cable and hardware for connection from ceiling rose complete as approved and directed by Engineer Incharge. Plastic body 10" dia | No. | 1 | 5568.1 | 5568.1
NS | Supply, Installation, testing and commissioning of Earthing set complete with accessories (Rod length should be 3 meter) as per drawings. To achieve Earthing value less than 1 Ohm, complete in all respects as approved by Engineer In charge. | Set | 1 | 25000 | 25000
Total |  |  |  |  | 63103.375
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority |  | Punjab Saaf Pani Authority

## WT
PUNJAB SAAF PANI AUTHORITY
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
Bill No 20: Water Analysis Reports
Sr, No | Description | Unit | Quantity | Unit Rate (RS) | Amount (RS)
1 | Water Quality Testing, Micro Biological Testing, Physical and Chemical Peramaters, Arsenic etc as per parameters recommended by engineer incharge | No. | 1
Total

## Rate Analysis (hidden)
Analysis for Non MRS Items
SKID Frame for Filtration Plant
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Repair & maintenance of Plant Skid frame and Finishing, complete in all respect, inclusive of Carriage to Site and Labor for Installation | 1 | Each | 10800 | 10800
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning of Plant skid at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 0
Contractor's Profit & Overheads 20%
| Total |  |  |  | 10800
| Say Rupees |  |  |  | 10800
Membrane Recovery
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Membranes recovery with chemicals cleaning, including labour & testing, Complete in all respects, inclusive of Carriage to Site and Labor for Installation | 1 | Each | 18000 | 18000
inclusive of Carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning of membrane at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 0
| Contractor's Profit & Overheads 20% |  |  |  | 0
| Total |  |  |  | 18000
| Say Rupees |  |  |  | 18000
Membrane Housing Supply
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & Commissioning of Membrane Housing, Complete in all respect | 1 | Each | 65000 | 65000
2 | Less 18% GST |  |  |  | 9915.2542
55084.7458
3 | Contractor's Profit & Overheads 20% |  |  |  | 11016.9492
| add 18% GST |  |  |  | 9915.2542
| Total |  |  |  | 76016.9492
| Say Rupees |  |  |  | 76015
| Say Rupees |  |  |  | 76015
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Cartridge Filter
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and Testing of Cartridge Filter complete in all respect | 1 | each | 1290 | 1290
2 | Less 18% GST |  |  |  | 196.7797
1093.2203
3 | Contractor's Profit & Overheads 20% |  |  |  | 218.6441
| add 18% GST |  |  |  | 196.7797
| Total |  |  |  | 1508.6441
| Say Rupees |  |  |  | 1510
TDS Meter
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and Testing of TDS meter complete with all respects | 1 | each | 10000 | 10000
2 | Less 18% GST |  |  |  | 1525.4237
8474.5763
3 | Contractor's Profit & Overheads 20% |  |  |  | 1694.9153
| add 18% GST |  |  |  | 1525.4237
| Total |  |  |  | 11694.9153
| Say Rupees |  |  |  | 11695
Pressure Switch
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and Testing of Pressure Switchs complete with all respects | 1 | each | 14000 | 14000
2 | Less 18% GST |  |  |  | 2135.5932
11864.4068
3 | Contractor's Profit & Overheads 20% |  |  |  | 2372.8814
| add 18% GST |  |  |  | 2135.5932
| Total |  |  |  | 16372.8814
| Say Rupees |  |  |  | 16375 | 4500
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Rota Meter
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and testing of Rota meter complete in all respect | 1 | each | 6000 | 6000
2 | Less 18% GST |  |  |  | 915.2542
5084.7458
3 | Contractor's Profit & Overheads 20% |  |  |  | 1016.9492
| add 18% GST |  |  |  | 915.2542
| Total |  |  |  | 7016.9492
| Say Rupees |  |  |  | 7015 | 1500
Pressure Gauges
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and Testing of pressure gauges, complete in all respect | 1 | each | 8500 | 8500
2 | Less 18% GST |  |  |  | 1296.6102
7203.3898
3 | Contractor's Profit & Overheads 20% |  |  |  | 1440.678
| add 18% GST |  |  |  | 1296.6102
| Total |  |  |  | 9940.678
| Say Rupees |  |  |  | 9940
Water Meter
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and testing of Water meter, complete in all respect | 1 | each | 15000 | 15000
2 | Less 18% GST |  |  |  | 2288.1356
12711.8644
3 | Contractor's Profit & Overheads 20% |  |  |  | 2542.3729
| add 18% GST |  |  |  | 2288.1356
| Total |  |  |  | 17542.3729
| Say Rupees |  |  |  | 17540
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Repair of Water Meter
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of water meter including callibration, complete in all respect | 1 | each | 5000 | 5000
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 5000
| Contractor's Profit & Overheads 20% |  |  |  | 1000
| Total |  |  |  | 6000
| Say Rupees |  |  |  | 6000
Solinoid Valve
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and Testing of Solinoid valve complete in all respect | 1 | each | 7500 | 7500
| Less 18% GST |  |  |  | 1144.0678
6355.9322
2 | Contractor's Profit & Overheads 20% |  |  |  | 1271.1864
| add 18% GST |  |  |  | 1144.0678
| Total |  |  |  | 8771.1864
| Say Rupees |  |  |  | 8770
Repair of Solinoid Valve
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of Solinoid valve complete in all respect | 1 | each | 3500 | 3500
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 3500
| Contractor's Profit & Overheads 20% |  |  |  | 700
| Total |  |  |  | 4200
| Say Rupees |  |  |  | 4200
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Multiport Valve
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation & Commissioning of 3way Multiport Valve, top & bottom distributers, complete in all respect | 1 | each | 35000 | 35000
2 | Less 18% GST |  |  |  | 5338.9831
29661.0169
3 | Contractor's Profit & Overheads 20% |  |  |  | 5932.2034
| add 18% GST |  |  |  | 5338.9831
| Total |  |  |  | 40932.2034
| Say Rupees |  |  |  | 40930
Repair of Multiport Valve
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of 3way Multiport Valve, top & bottom distributers, complete in all respect | 1 | each | 7000 | 7000
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 7000
| Contractor's Profit & Overheads 20% |  |  |  | 1400
| Total |  |  |  | 8400
| Say Rupees |  |  |  | 8400
Antiscalant / Chlorinator / Dosing Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply, installation and Testing of Chemical Dosing Pump, Chlorinator / Liqued Dosing Pump with working pressure 5 - 7 Bar Imported, along with 80 liter capacity tank with all repects.complete in all respect | 1 | Each | 59200 | 59200
2 | Less 18% GST |  |  |  | 9030.5085
50169.4915
3 | Contractor's Profit & Overheads 20% |  |  |  | 10033.8983
| add 18% GST |  |  |  | 9030.5085
| Total |  |  |  | 69233.8983
| Say Rupees |  |  |  | 69235
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Water Storage Tank
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply and installation of Water Storage Tank, Capacity 2000 Liters, Material PE, Food Grade, complete in all respects | 1 | Each | 27000 | 27000
2 | Less 18% GST |  |  |  | 4118.6441
22881.3559
3 | Contractor's Profit & Overheads 20% |  |  |  | 4576.2712
| add 18% GST |  |  |  | 4118.6441
| Total |  |  |  | 31576.2712
| Say Rupees |  |  |  | 31575
Cleaning of Water Storage Tank
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Chemical Cleaning & repair of Water Storage tank, complete in all respects at site | 1 | Each | 5000 | 5000
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 5000
| Contractor's Profit & Overheads 20% |  |  |  | 1000
| Total |  |  |  | 6000
| Say Rupees |  |  |  | 6000
Float Switch
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply and installation of float switch for Water Storage Tank, complete in all respect | 1 | Each | 2500 | 2500
2 | Less 18% GST |  |  |  | 381.3559
2118.6441
3 | Contractor's Profit & Overheads 20% |  |  |  | 423.7288
| add 18% GST |  |  |  | 381.3559
| Total |  |  |  | 2923.7288
| Say Rupees |  |  |  | 2925
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Activated Carbon Media Replacment
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Replacement of Activated Carbon media supply, installation and commissioning complete in all respect NSF Certified, Iodin No 900-1100 | 1 | Kg | 1260 | 1260
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Total |  |  |  | 1260
| Contractor's Profit & Overheads 20% |  |  |  | 252
| Total |  |  |  | 1512
| Say Rupees |  |  |  | 1510
Silica Sand Media Replacment
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Replacement of Silica sand media supply, installation and commissioning complete in all respect | 1 | Kg | 90 | 90
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Total |  |  |  | 90
| Contractor's Profit & Overheads 20% |  |  |  | 18
| Total |  |  |  | 108
| Say Rupees |  |  |  | 110
Natural Gravels Media Replacment
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Replacement of Natural Gravels media supply, installation and commissioning complete in all respect | 1 | Kg | 90 | 90
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Total |  |  |  | 90
| Contractor's Profit & Overheads 20% |  |  |  | 18
| Total |  |  |  | 108
| Say Rupees |  |  |  | 110
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Arsenic Media Replacment
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Replacement of Granular Feric Oxide use for druinking water treatment with oxidation capavity of AS3 to AS5, commissioning complete in all respect | 1 | Kg | 2200 | 2200
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Total |  |  |  | 2200
| Contractor's Profit & Overheads 20% |  |  |  | 440
| Total |  |  |  | 2640
| Say Rupees |  |  |  | 2640
UV Lamp
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of UV lamp complete in all respect | 1 | Each | 20000 | 20000
| Less 18% GST |  |  |  | 3050.8475
16949.1525
3 | Contractor's Profit & Overheads 20% |  |  |  | 3389.8305
| add 18% GST |  |  |  | 3050.8475
| Total |  |  |  | 23389.8305
| Say Rupees |  |  |  | 23390
Manual Valve
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & Commissioning of Manual Valve complete in all respect | 1 | Each | 3000 | 3000
| Less 18% GST |  |  |  | 457.6271
2542.3729
3 | Contractor's Profit & Overheads 20% |  |  |  | 508.4746
| add 18% GST |  |  |  | 457.6271
| Total |  |  |  | 3508.4746
| Say Rupees |  |  |  | 3510
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Repair of Pipe Fitting
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Repair & maintenance of Pipe and fittings, complete plant fitting in all respect | 1 | Each | 10000 | 10000
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Total |  |  |  | 10000
| Contractor's Profit & Overheads 20% |  |  |  | 2000
| Total |  |  |  | 12000
| Say Rupees |  |  |  | 12000
Plastic Water Taps
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation & testing of Plastic water Taps with fussion joint, complete in all respect | 1 | Each | 500 | 500
2 | Less 18% GST |  |  |  | 76.2712
423.7288
3 | Contractor's Profit & Overheads 20% |  |  |  | 84.7458
| add 18% GST |  |  |  | 76.2712
| Total |  |  |  | 584.7458
| Say Rupees |  |  |  | 585
Repair of RO Plant Electric Controller
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Repair & maintenance of Plant control panel with PLC & HMI complete in all respect | 1 | Each | 32000 | 32000
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Total |  |  |  | 32000
| Contractor's Profit & Overheads 12.5% |  |  |  | 4000
| Total |  |  |  | 36000
| Say Rupees |  |  |  | 36000
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Washing of Bore Hole
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Repairing, Cleaning & Washing existing bore holes by using air compresseor or any other equipment | 1 | Each | 42000 | 42000
Inclusive of carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 42000
| Contractor's Profit & Overheads 20% |  |  |  | 8400
| Total |  |  |  | 50400
| Say Rupees |  |  |  | 50400
Water Quality Testing
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Water Quality Testing, Micro Biological Testing, Physical and Chemical Peramaters, Arsenic etc as per parameters recommended by engineer incharge | 1 | Each | 5100 | 5100
| Total |  |  |  | 5100
| Say Rupees |  |  |  | 5100
Safety Strainer
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply and installation of safety filter strainer | 1 | each | 1200 | 1200
2 | Less 18% GST |  |  |  | 183.0508
1016.9492
3 | Contractor's Profit & Overheads 20% |  |  |  | 203.3898
| add 18% GST |  |  |  | 183.0508
| Total |  |  |  | 1403.3898
| Say Rupees |  |  |  | 1405
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
FRP Vessel (16" x 65")
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and commissioning of FRP Vessel size (16" x 65") for media filtration, complete in all respects | 1 | each | 58000 | 58000
2 | Less 18% GST |  |  |  | 8847.4576
49152.5424
3 | Contractor's Profit & Overheads 20% |  |  |  | 9830.5085
| add 18% GST |  |  |  | 8847.4576
| Total |  |  |  | 67830.5085
| Say Rupees |  |  |  | 67830
FRP Vessel (24" x 72")
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and commissioning of FRP Vessel size (24" x 72") for media filtration, complete in all respects | 1 | each | 140000 | 140000
2 | Less 18% GST |  |  |  | 21355.9322
118644.0678
3 | Contractor's Profit & Overheads 20% |  |  |  | 23728.8136
| add 18% GST |  |  |  | 21355.9322
| Total |  |  |  | 163728.8136
| Say Rupees |  |  |  | 163730

## RA RO500 (hidden)
Analysis for Non MRS Items
RO Membrane 500 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installtion and commissioning of RO Plant membranes(4x40), 2 No. complete in all respect | 1 | Each | 90000 | 90000
2 | Less 18% GST |  |  |  | 13728.8136
76271.1864
3 | Contractor's Profit & Overheads 20% |  |  |  | 15254.2373
| add 18% GST |  |  |  | 13728.8136
| Total |  |  |  | 105254.2373
| Say Rupees |  |  |  | 105255
RO Feed Pump for 500 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation and commissioning of RO Feed Pump capacity of 1000 LPH, for 500 LPH RO Plant, complete in all respect | 1 | Each | 62500 | 62500
2 | Less 18% GST |  |  |  | 9533.8983
52966.1017
3 | Contractor's Profit & Overheads 20% |  |  |  | 10593.2203
| add 18% GST |  |  |  | 9533.8983
| Total |  |  |  | 73093.2203
| Say Rupees |  |  |  | 73095
High Pressure Pump for RO 500 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply, Installation and commissioning of RO High Pressure Pump Capacity of 1000 LPH, for 500 LPH RO Plant, complete in all respect | 1 | Each | 140000 | 140000
2 | Less 18% GST |  |  |  | 21355.9322
118644.0678
3 | Contractor's Profit & Overheads 20% |  |  |  | 23728.8136
| add 18% GST |  |  |  | 21355.9322
| Total |  |  |  | 163728.8136
| Say Rupees |  |  |  | 163730
RO Feed Pump Repair 500 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of RO Feed water pump 1000 LPH, for 500 LPH RO Plant, complete in all respect | 1 | each | 20000 | 20000 | s
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 2000 | 2000
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 2000 | 2000
| Total |  |  |  | 24000
| Contractor's Profit & Overheads 20% |  |  |  | 4800
| Total |  |  |  | 28800
| Say Rupees |  |  |  | 28800
RO High Pressure Pump Repair 500 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of RO High Pressure pump 1000 LPH, for 500 LPH RO Plant, complete in all respect | 1 | each | 30000 | 30000
2 | Carriage Market to Site | 1 | P/Job | 2000 | 2000
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 2000 | 2000
| Total |  |  |  | 34000
| Contractor's Profit & Overheads 20% |  |  |  | 6800
| Total |  |  |  | 40800
| Say Rupees |  |  |  | 40800
RO 500 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of 500 L/H Reverse Osmosis (RO) Plant for TDS removal up to 5000 mg/l and inclusive of all taxes conforming to standard specifications according to the Punjab Aab-e-Pak Authority. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | 1 | Each | 1025000 | 1025000
2 | Less 18% GST |  |  |  | 156355.9322
| Total |  |  |  | 868644.0678
3 | Contractor's Profit & Overheads 20% |  |  |  | 173728.8136
| add 18% GST |  |  |  | 156355.9322
| Total |  |  |  | 1198728.8136
| Say Rupees |  |  |  | 1198730
Submursible Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | 1 | Each | 99500 | 99500
2 | Less 18% GST |  |  |  | 15177.9661
84322.0339
3 | Contractor's Profit & Overheads 20% |  |  |  | 16864.4068
| add 18% GST |  |  |  | 15177.9661
| Total |  |  |  | 116364.4068
| Say Rupees |  |  |  | 116365

## RA RO1000 (hidden)
Analysis for Non MRS Items
RO Membrane 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installtion and commissioning of RO Plant membranes(4x40), 2 No. complete in all respect | 2 | Each | 90000 | 180000
2 | Less 18% GST |  |  |  | 27457.6271
152542.3729
3 | Contractor's Profit & Overheads 20% |  |  |  | 30508.4746
| add 18% GST |  |  |  | 27457.6271
| Total |  |  |  | 210508.4746
| Say Rupees |  |  |  | 210510
RO Feed Pump for 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation and commissioning of RO Feed Pump capacity of 2000 LPH, for 1000 LPH RO Plant, complete in all respect | 1 | Each | 87000 | 87000
2 | Less 18% GST |  |  |  | 13271.1864
73728.8136
3 | Contractor's Profit & Overheads 20% |  |  |  | 14745.7627
| add 18% GST |  |  |  | 13271.1864
| Total |  |  |  | 101745.7627
| Say Rupees |  |  |  | 101745
High Pressure Pump for RO 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply, Installation and commissioning of RO High Pressure Pump Capacity of 2000 LPH, for 1000 LPH RO Plant, complete in all respect | 1 | Each | 175000 | 175000
2 | Less 18% GST |  |  |  | 26694.9153
148305.0847
3 | Contractor's Profit & Overheads 20% |  |  |  | 29661.0169
| add 18% GST |  |  |  | 26694.9153
| Total |  |  |  | 204661.0169
| Say Rupees |  |  |  | 204660
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
RO Feed Pump Repair 1000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of RO Feed water pump 2000 LPH, for 1000 LPH RO Plant, complete in all respect | 1 | each | 24000 | 24000
inclusive of Carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 24000
| Contractor's Profit & Overheads 20% |  |  |  | 4800
| Total |  |  |  | 28800
| Say Rupees |  |  |  | 28800
RO High Pressure Pump Repair 1000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of RO High Pressure pump 2000 LPH, for 1000 LPH RO Plant, complete in all respect | 1 | each | 34000 | 34000
inclusive of Carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 34000
| Contractor's Profit & Overheads 20% |  |  |  | 6800
| Total |  |  |  | 40800
| Say Rupees |  |  |  | 40800
RO 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of 1000 L/H Reverse Osmosis (RO) Plant for TDS removal up to 5000 mg/l and inclusive of all taxes conforming to standard specifications according to the Punjab Aab-e-Pak Authority. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | 1 | Each | 1650000 | 1650000
2 | Less 18% GST |  |  |  | 251694.9153
| Total |  |  |  | 1398305.0847
3 | Contractor's Profit & Overheads 20% |  |  |  | 279661.0169
| add 18% GST |  |  |  | 251694.9153
| Total |  |  |  | 1929661.0169
| Say Rupees |  |  |  | 1929660
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Submersible Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | 1 | Each | 99500 | 99500
2 | Less 18% GST |  |  |  | 15177.9661
84322.0339
3 | Contractor's Profit & Overheads 20% |  |  |  | 16864.4068
| add 18% GST |  |  |  | 15177.9661
| Total |  |  |  | 116364.4068
| Say Rupees |  |  |  | 116365
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
5.5 KW Solar System
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and commissioning of 5.5 KW Solar System for RO 1000 LPH mounted on civil & Steel structure, VFD's etc complete in all respects | 1 | each | 1136000 | 1136000
2 | Less 18% GST |  |  |  | 173288.1356
962711.8644
3 | Contractor's Profit & Overheads 20% |  |  |  | 192542.3729
| add 18% GST |  |  |  | 173288.1356
| Total |  |  |  | 1328542.3729
| Say Rupees |  |  |  | 1328540

## RA UF1000 (hidden)
Analysis for Non MRS Items
UF Membrane 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installtion and commissioning of UF Plant membranes. complete in all respect | 2 | Each | 65000 | 130000
2 | Less 18% GST |  |  |  | 19830.5085
110169.4915
3 | Contractor's Profit & Overheads 20% |  |  |  | 22033.8983
| add 18% GST |  |  |  | 19830.5085
| Total |  |  |  | 152033.8983
| Say Rupees |  |  |  | 152035
UF Feed Pump for 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation and commissioning of UF Feed Pump capacity of 1000 LPH, for 1000 LPH UF Plant, complete in all respect | 1 | Each | 62500 | 62500
2 | Less 18% GST |  |  |  | 9533.8983
52966.1017
3 | Contractor's Profit & Overheads 20% |  |  |  | 10593.2203
| add 18% GST |  |  |  | 9533.8983
| Total |  |  |  | 73093.2203
| Say Rupees |  |  |  | 73095
UF Feed Pump Repair 1000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of UF Feed water pump 1000 LPH, for 1000 LPH UF Plant, complete in all respect | 1 | each | 20000 | 20000
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 2000 | 2000
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 2000 | 2000
| Total |  |  |  | 24000
| Contractor's Profit & Overheads 20% |  |  |  | 4800
| Total |  |  |  | 28800
| Say Rupees |  |  |  | 28800
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
UF 1000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of 1000 L/H Ultra Filtration (UF) Plant for removal of Bacteriological & other contaminants and inclusive of all taxes conforming to standard specifications of filtration plants. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | 1 | Each | 1445000 | 1445000
2 | Less 18% GST |  |  |  | 220423.7288
| Total |  |  |  | 1224576.2712
3 | Contractor's Profit & Overheads 20% |  |  |  | 244915.2542
| add 18% GST |  |  |  | 220423.7288
| Total |  |  |  | 1689915.2542
| Say Rupees |  |  |  | 1689915
Submursible Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | 1 | Each | 99500 | 99500
2 | Less 18% GST |  |  |  | 15177.9661
84322.0339
3 | Contractor's Profit & Overheads 20% |  |  |  | 16864.4068
| add 18% GST |  |  |  | 15177.9661
| Total |  |  |  | 116364.4068
| Say Rupees |  |  |  | 116365
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
3 KW Solar System
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and commissioning of 3 KW Solar System for UF 1000 LPH mounted on civil & Steel structure, VFD's etc complete in all respects | 1 | each | 825000 | 825000
2 | Less 18% GST |  |  |  | 125847.4576
699152.5424
3 | Contractor's Profit & Overheads 20% |  |  |  | 139830.5085
| add 18% GST |  |  |  | 125847.4576
| Total |  |  |  | 964830.5085
| Say Rupees |  |  |  | 964830

## RA RO2000 (hidden)
Analysis for Non MRS Items
RO Membrane 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installtion and commissioning of RO Plant membranes(4x40), 4 No. complete in all respect. inclusive of Carriage to Site and Labor for Installation | 4 | Each | 90000 | 360000
2 | Less 18% GST |  |  |  | 54915.2542
305084.7458
3 | Contractor's Profit & Overheads 20% |  |  |  | 61016.9492
| add 18% GST |  |  |  | 54915.2542
| Total |  |  |  | 421016.9492
| Say Rupees |  |  |  | 421015
RO Feed Pump for 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation and commissioning of RO Feed Pump capacity of 4000 LPH, for 2000 LPH RO Plant, complete in all respect | 1 | Each | 102000 | 102000
2 | Less 18% GST |  |  |  | 15559.322
86440.678
3 | Contractor's Profit & Overheads 20% |  |  |  | 17288.1356
| add 18% GST |  |  |  | 15559.322
| Total |  |  |  | 119288.1356
| Say Rupees |  |  |  | 119290
High Pressure Pump for RO 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply, Installation and commissioning of RO High Pressure Pump Capacity of 4000 LPH, for 2000 LPH RO Plant, complete in all respect | 1 | Each | 205000 | 205000
2 | Less 18% GST |  |  |  | 31271.1864
173728.8136
3 | Contractor's Profit & Overheads 20% |  |  |  | 34745.7627
| add 18% GST |  |  |  | 31271.1864
| Total |  |  |  | 239745.7627
| Say Rupees |  |  |  | 239745
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
RO Feed Pump Repair 2000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of RO Feed water pump 4000 LPH, for 2000 LPH RO Plant, complete in all respect | 1 | each | 24000 | 24000
inclusive of Carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 24000
| Contractor's Profit & Overheads 20% |  |  |  | 4800
| Total |  |  |  | 28800
| Say Rupees |  |  |  | 28800
RO High Pressure Pump Repair 2000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of RO High Pressure pump 4000 LPH, for 2000 LPH RO Plant, complete in all respect | 1 | each | 34000 | 34000
inclusive of Carriage to Site and Labor for Installation
2 | Carriage Market to Site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 34000
| Contractor's Profit & Overheads 20% |  |  |  | 6800
| Total |  |  |  | 40800
| Say Rupees |  |  |  | 40800
RO 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of 2000 L/H Reverse Osmosis (RO) Plant for TDS removal up to 5000 mg/l and inclusive of all taxes conforming to standard specifications according to the Punjab Aab-e-Pak Authority. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | 1 | Each | 2250000 | 2250000
2 | Less 18% GST |  |  |  | 343220.339
| Total |  |  |  | 1906779.661
3 | Contractor's Profit & Overheads 20% |  |  |  | 381355.9322
| add 18% GST |  |  |  | 343220.339
| Total |  |  |  | 2631355.9322
| Say Rupees |  |  |  | 2631355
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Submursible Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | 1 | Each | 99500 | 99500
2 | Less 18% GST |  |  |  | 15177.9661
84322.0339
3 | Contractor's Profit & Overheads 20% |  |  |  | 16864.4068
| add 18% GST |  |  |  | 15177.9661
| Total |  |  |  | 116364.4068
| Say Rupees |  |  |  | 116365
Water Quality Testing
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Water Quality Testing, Micro Biological Testing, Physical and Chemical Peramaters, Arsenic etc as per parameters recommended by engineer incharge | 1 | Each | 9000 | 9000
2 | Less 18% GST |  |  |  | 1372.8814
7627.1186
3 | Contractor's Profit & Overheads 20% |  |  |  | 1525.4237
| add 18% GST |  |  |  | 1372.8814
| Total |  |  |  | 10525.4237
| Say Rupees |  |  |  | 10525
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity

## RA UF2000 (hidden)
Analysis for Non MRS Items
UF Membrane 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installtion and commissioning of UF Plant membranes(4x40), 2 No. complete in all respect | 4 | Each | 65000 | 260000
2 | Less 18% GST |  |  |  | 39661.0169
220338.9831
3 | Contractor's Profit & Overheads 20% |  |  |  | 44067.7966
| add 18% GST |  |  |  | 39661.0169
| Total |  |  |  | 304067.7966
| Say Rupees |  |  |  | 304070
UF Feed Pump for 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation and commissioning of UF Feed Pump capacity of 2000 LPH, for 2000 LPH UF Plant, complete in all respect | 1 | Each | 87000 | 87000
2 | Less 18% GST |  |  |  | 13271.1864
73728.8136
3 | Contractor's Profit & Overheads 20% |  |  |  | 14745.7627
| add 18% GST |  |  |  | 13271.1864
| Total |  |  |  | 101745.7627
| Say Rupees |  |  |  | 101745
UF Feed Pump Repair 2000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of UF Feed water pump 2000 LPH, for 2000 LPH UF Plant, complete in all respect | 1 | each | 24000 | 24000
inclusive of Carriage to Site and Labor for Installation
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 0 | 0
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 0 | 0
| Total |  |  |  | 24000
| Contractor's Profit & Overheads 20% |  |  |  | 4800
| Total |  |  |  | 28800
| Say Rupees |  |  |  | 28800
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
UF 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of 2000 L/H Ultra Filtration (UF) Plant for removal of Bacteriological & other contaminants and inclusive of all taxes conforming to standard specifications of filtration plants. The specifications along with equipment and accessories properly mounted in the SS frame/skid. | 1 | Each | 2167000 | 2167000
2 | Less 18% GST |  |  |  | 330559.322
| Total |  |  |  | 1836440.678
3 | Contractor's Profit & Overheads 20% |  |  |  | 367288.1356
| add 18% GST |  |  |  | 330559.322
| Total |  |  |  | 2534288.1356
| Say Rupees |  |  |  | 2534290
Submersible Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | 1 | Each | 99500 | 99500
2 | Less 18% GST |  |  |  | 15177.9661
84322.0339
3 | Contractor's Profit & Overheads 20% |  |  |  | 16864.4068
| add 18% GST |  |  |  | 15177.9661
| Total |  |  |  | 116364.4068
| Say Rupees |  |  |  | 116365
Water Quality Testing
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Water Quality Testing, Micro Biological Testing, Physical and Chemical Peramaters, Arsenic etc as per parameters recommended by engineer incharge | 1 | Each | 9000 | 9000
2 | Less 18% GST |  |  |  | 1372.8814
7627.1186
3 | Contractor's Profit & Overheads 20% |  |  |  | 1525.4237
| add 18% GST |  |  |  | 1372.8814
| Total |  |  |  | 10525.4237
| Say Rupees |  |  |  | 10525
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity

## RA MF2000 (hidden)
Analysis for Non MRS Items
MF Feed Pump for 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation and commissioning of MF Feed Pump capacity of 2000 LPH, for 2000 LPH MF Plant, complete in all respect | 1 | Each | 87000 | 87000
2 | Less 18% GST |  |  |  | 13271.1864
73728.8136
3 | Contractor's Profit & Overheads 20% |  |  |  | 14745.7627
| add 18% GST |  |  |  | 13271.1864
| Total |  |  |  | 101745.7627
| Say Rupees |  |  |  | 101745
MF Feed Pump Repair 2000 LPH
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Repair & maintenance of MF Feed water pump 2000 LPH, for 2000 LPH MF Plant, complete in all respect | 1 | each | 24000 | 24000
2 | Carriage Site to workshop and workshop to site | 1 | P/Job | 2000 | 2000
3 | Laboure for fixing, Installation & Commissioning at site | 1 | P/Job | 2000 | 2000
| Total |  |  |  | 28000
| Contractor's Profit & Overheads 20% |  |  |  | 5600
| Total |  |  |  | 33600
| Say Rupees |  |  |  | 33600
MF 2000 LPH
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply installation and commissioning of 2000 L/H Multimedia Filtration (MF) Plant, inclusive of all taxes, conforming to standard specifications of filtration plants. The specifications along with equipment and accessories properly mounted on the SS frame/skid. | 1 | Each | 545000 | 545000 | 2000 L/H Pre Filtration Plant, inclusive of all taxes, conforming to standard specifications of filtration plants. The specifications along with equipment and accessories properly mounted in the frame/skid.
2 | Less 18% GST |  |  |  | 83135.5932
| Total |  |  |  | 461864.4068
3 | Contractor's Profit & Overheads 20% |  |  |  | 92372.8814
| add 18% GST |  |  |  | 83135.5932
| Total |  |  |  | 637372.8814
| Say Rupees |  |  |  | 637375
Submursible Pump
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply Installation & commissioning of 3inch submersible pump 3HP including supporting clamp, pump coupling, cable clip, delivery pipe, cable complete in all respect. | 1 | Each | 99500 | 99500
2 | Less 18% GST |  |  |  | 15177.9661
84322.0339
3 | Contractor's Profit & Overheads 20% |  |  |  | 16864.4068
| add 18% GST |  |  |  | 15177.9661
| Total |  |  |  | 116364.4068
| Say Rupees |  |  |  | 116365
Water Quality Testing
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Water Quality Testing, Micro Biological Testing, Physical and Chemical Peramaters, Arsenic etc as per parameters recommended by engineer incharge | 1 | Each | 9000 | 9000
2 | Less 18% GST |  |  |  | 1372.8814
7627.1186
3 | Contractor's Profit & Overheads 20% |  |  |  | 1525.4237
| add 18% GST |  |  |  | 1372.8814
| Total |  |  |  | 10525.4237
| Say Rupees |  |  |  | 10525
5.5 KW Solar System
Detail |  | Qty | Unit | Unit Rate | Amount
1 | Supply Installation and commissioning of 5.5 KW Solar System for UF 2000 LPH mounted on civil & Steel structure, VFD's etc complete in all respects | 1 | each | 1136000 | 1136000
2 | Less 18% GST |  |  |  | 173288.1356
962711.8644
3 | Contractor's Profit & Overheads 20% |  |  |  | 192542.3729
| add 18% GST |  |  |  | 173288.1356
| Total |  |  |  | 1328542.3729
| Say Rupees |  |  |  | 1328540

## Injection well (hidden)
#REF!
Injection Well for Brine
Sr. No. | MRS | Description of items | Unit | Qty | Rate | Total Amount (Rs)
SCHEDULE ITEMS BASED ON MRS, 2nd BI-ANNUAL PERIOD (1st Jun, 2024 TO 30th Dec, 2024) Lahore
1 | 23-3-b | Boring for tubewell in all types of soil except shingle, gravel & rock, from a depth of 0 to 100 (0 to 30 m) below ground level, including sinking and withdrawing of casing pipe, complete:-
|  |  | M | 30 | 4052.75 | 121582.5
1 | 23-3-b | Boring for tubewell in all types of soil except shingle, gravel & rock, from a depth of 100.1 ft. to 200 ft. (30 to 60 m) below ground level, including sinking and withdrawing of casing pipe, complete:-
|  |  | M | 30 | 6289.1 | 188673
1 | 23-3-b | Boring for tubewell in all types of soil except shingle, gravel & rock, from a depth of 200.1 ft. to 300 ft. (60 to 90 m) below ground level, including sinking and withdrawing of casing pipe, complete:-
|  |  | M | 30 | 8049.3 | 241479
3 | 6-5-f | Cement concrete plain including placing, compacting, finishing and curing complete (including screening and washing of stone aggregate): Ratio 1: 2: 4
|  |  | Cu.m | 0.5 | 17024.15 | 8512.075
4 | 6-6-a ii b(i) | (a)(ii)Reinforced cement concrete in retaining/Shear walls laid in situ or precasted in position,or pre stressed members cast ins itu(Formwork on both sides) , complete in all respects: Type C (nominal mix 1:2:4) Upto 9" thick (Avg)
|  |  | Cu.m | 1.5 | 25909.85 | 38864.775
5 | 23-13-iii | Providing and installing P.V.C. Bail/End plug, in tubewell bore hole:- (4" dia). (100 mm)
|  |  | Each | 1 | 142.2 | 142.2
6 | 23-11-b | Providing and installing, P.V.C. strainer B.S.S. Class 'B' in tubewell bore hole, including sockets and solvents, etc. complete . 4" dia (100mm).
|  |  | per M | 22 | 1058 | 23276
7 | 23-17-b | Providing and installing P.V.C. blind pipe, B.S.S. Class `B', in tubewell bore hole, including sockets and solvents and jointing with strainer, etc. complete (4" dia)
|  |  | M | 75 | 1917.85 | 143838.75
8 | N.S | Providing, fixing, jointing and testing Polypropylene Random Copolymer (PPRC) PN20 pressure pipe for cold and hot water as per DIN 8077-8078, PN 20 for pipes and DIN 16962, PN 25 for fittings (polyfusion welded joints) inside building including fittings and specials (sockets, tees, elbows, bends, crosses, reducers, adaptor, plugs and union etc.) supported on walls or suspended from roof slab or run in chases including pipe hangers, supports, cutting and making good the chases and holes, complete in all respects.
|  |  | M | 10 | 1500 | 15000
9 | N.S | Supply & installation of 1/2" i/d thick M.S Cap for 6" housing pipe joint by means of welding & hinges with lock & locking arrangements.
|  |  | Each | 1 | 2522.81 | 2522.81
10 | N.S | Taking of water samples (2 bottles each) at the end of the pumping test. Full chemical and bacteriological analysis, of water samples according to WHO.
|  |  | Each | 1 | 8000 | 8000
UNIT COST: | [5 empty] | 481635.61

## HR for Projects (hidden)
REHABILITATION OF WATER FILTRATION PLANTS IN DISTRICT BAHAWALPUR
Humen Resource / Staff for Supervision of Projects
Sr. No. | Activity | Unit | Quantity | Salary per Month | Total Cost
1 | Graduate Engineer (Resident at site) | No | 2 | 88790 | 177580
2 | Sub Engineer DAE (Resident at site) | No | 3 | 46422 | 139266
3 | Unskilled Labour | No | 2 | 32000 | 64000
4 | Rental Field Vehicle | No | 2 | 100000 | 200000
5 | POL for Field Vehicle | No | 2 | 72000 | 144000
Total per Month:- |  |  |  |  | 724846
Total for 3 Months:- |  |  |  |  | 2174538
say (in million) |  |  |  |  | 2.1745

## O&M Analysis (hidden)
1 Year O&M for RO/MF/UF PLANTS
O&M Analysis
Sr. No. | Description | Unit | BILL NO 1 - 01 Year
Reverse Osmosis - 2000 LPH
|  |  | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE Or Safety Strainer for Media Filtration | No | 12 | 1510 | 18120
2 | Plant Operator, 1 Nos. | Man Months | 12 | 32000 | 384000
3 | Water Testing (From ISO Approved Lab) | Quarterly | 4 | 5100 | 20400
4 | Visit of Technical Staff | Quarterly | 4 | 7200 | 28800
5 | Antiscalent Chemical (DOSING) Manufacturer: Europe/USA/Equv Dosing Rate: 5 Ppm | Kg | 24 | 1580 | 37920
6 | Sodium Hypochlorite | Kg | - | - | -
7 | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Manufacturer: Europe/USA/Equv Dosing Rate: 8 Ppm Acidic/Alkaline | No. | 2 | 18000 | 36000
6 | Over Head Expense / Miscellaneous | Per Year | 1 | 9999.6 | 9999.6
TOTAL COST |  |  |  | (A ) | 535239.6
Sr. No. | Description | Unit | BILL NO 2 - 01 Year
Media Filtration - 2000 LPH
|  |  | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE Or Safety Strainer for Media Filtration | No | 12 | 1510 | 18120
2 | Plant Operator, 1 Nos. | Man Months | 12 | 32000 | 384000
3 | Water Testing (From ISO Approved Lab) | Quarterly | 4 | 5100 | 20400
4 | Visit of Technical Staff | Quarterly | 4 | 7200 | 28800
5 | Sodium Hypochlorite | Kg | 18 | 491.7949 | 8852.3077
6 | Over Head Expense / Miscellaneous | Per Year | 1 | 9999.6 | 9999.6
TOTAL COST |  |  |  | (B) | 470171.9077
Sr. No. | Description | Unit | BILL NO 3 - 01 Year
UF Filtration - 2000 LPH
|  |  | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE Or Safety Strainer for Media Filtration | No | 12 | 1510 | 18120
2 | Plant Operator, 1 Nos. | Man Months | 12 | 32000 | 384000
3 | Water Testing (From ISO Approved Lab) | Quarterly | 4 | 5100 | 20400
4 | Visit of Technical Staff | Quarterly | 4 | 7200 | 28800
5 | Sodium Hypochlorite | Kg | 18 | 491.7949 | 8852.3077
6 | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Manufacturer: Europe/USA/Equv Dosing Rate: 8 Ppm Acidic/Alkaline | No. | 2 | 18000 | 36000
7 | Over Head Expense / Miscellaneous | Per Year | 1 | 9999.6 | 9999.6
TOTAL COST |  |  |  | (C) | 506171.9077
O&M for 43 Rehabilitated Plants for 1 Year |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 | A - 1 Year O&M for RO Plants | No. | 31 | 535239.6 | 16592427.6
2 | B - 1 Year O&M for MF Plants | No. | 0 | 470171.9077 | 0
3 | C - 1 Year O&M for UF Plants | No. | 41 | 506171.9077 | 20753048.2154 |  | 1511583.4154
| Total (A+B+C) |  |  |  | 37345475.8154 |  | 503861.1385
0.50386
TOTAL YEARLY COST FOR O&M WITHOUT ELECTRICITY (A+B+C) |  |  |  |  | 37345475.8154
ADD 16% PRA |  |  |  |  | 5975276.1305
GRAND TOTAL |  |  |  |  | 43320751.9458
AMOUNT IN MILLION |  |  |  |  | 43.3208
ELECTRICITY BILL FOR 12 MONTHS
|  | Ro Electricity Charges | Media Filter Electricity Charges | UF Electricity Charges
| Lum Sum Base Rate Per Plant /Month | 45000 | 20000 | 30000
| No of plants | 31 | 0 | 41
| Amount of Electricity for 12 months | 16740000 | 0 | 14760000
| Amount of Electricity Charges for 1 Year | 31500000
O&M for 190 Plants for 1 Year |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 | A - 1 Year O&M for RO Plants | No. | 154 | 535239.6 | 82426898.4
2 | B - 1 Year O&M for UF Plants | No. | 27 | 506171.9077 | 13666641.5077
3 | C - 1 Year O&M for MF Plants | No. | 9 | 470171.9077 | 4231547.1692
| Total (A+B+C) |  |  |  | 100325087.0769
TOTAL YEARLY COST FOR O&M WITHOUT ELECTRICITY (A+B+C) |  |  |  |  | 100325087.0769
ADD 16% PRA |  |  |  |  | 16052013.9323
GRAND TOTAL |  |  |  |  | 116377101.0092
AMOUNT IN MILLION |  |  |  |  | 116.3771
ELECTRICITY BILL FOR 12 MONTHS
|  | Ro Electricity Charges | Media Filter Electricity Charges | UF Electricity Charges | Rehab Out Standing Electricity Charges
| Lum Sum Base Rate Per Plant /Month | 45000 | 20000 | 25000 | 100000
| No of plants | 154 | 27 | 9 | 72
| Amount of Electricity for 12 months | 83160000 | 6480000 | 2700000 | 7200000
| Amount of Electricity Charges for 1 Year | 99540000
| Total Cost for the O&M of 190 Plants in Bahawalpur District | 116377101.0092 | 116.3771 | 0.61251 | 215917101.0092 | 215.9171
| Total Electricity Charges for the Rehab & Functional Plants | 99540000 | 99.54 |  |  | 1.1364
Note on D10: Talha Khan Niazi: 04 KG per plant per month, we took 2 litr for 8 hour operational… we took 4 kg per plant / month
Note on D12: Talha Khan Niazi: 1 cip per year, 6 litr per plant per year
Note on E12: Talha Khan Niazi: taken fron center TS

## O&M Abs 06 Months (hidden)
06 Months O&M for RO (1000 LPH, 2000 LPH) & UF (2000 LPH) PLANTS
BILL NO 1 - Cost of O&M of 01 Plant for 06 Months
Sr. No. | Non-MRS | Description | Reverse Osmosis - 500 LPH
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.) | 97.2
1 |  | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE | No | 36 | 1510 | 54360
2 |  | Plant Operator, 1 Nos. | Man Months | 6 | 37000 | 222000 | Anti Scalent Calculation | 14.4
3 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2 | 5100 | 10200
4 |  | Antiscalent Chemical (DOSING) Dosing Rate: 5 Ppm | Kg | 28.8 | 1580 | 45504 | 7.2 | 54 | 36.4
5 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | Per Job | 1 | 2338.9831 | 2338.9831 | 3.6 | 324 | 324
TOTAL COST |  |  |  | (A ) |  | 334402.9831
BILL NO 2 - Cost of O&M of 01 Plant for 06 Months
Sr. No. | Non-MRS | Description | Media Filtration - 1000 LPH
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.) | 97.2
1 |  | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE | No | 36 | 1510 | 54360
2 |  | Plant Operator, 1 Nos. | Man Months | 6 | 37000 | 222000 | Anti Scalent Calculation | 14.4
3 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2 | 5100 | 10200
4 |  | Antiscalent Chemical (DOSING) Dosing Rate: 5 Ppm | Kg | 14.4 | 1580 | 22752 |  | 54 | 36.4
5 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | Per Job | 1 | 2339 | 2339 |  | 324 | 324
TOTAL COST |  |  |  | (B ) |  | 311651
BILL NO 3 - Cost of O&M of 01 Plant for 06 Months
Sr. No. | Non MRS | Description | UF Plant - 2000/1000/4000 LPH
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 |  | Plant Operator, 1 Nos. | Man Months | 6 | 37000 | 222000
2 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2 | 5100 | 10200
3 |  | Antiscalent Chemical (DOSING) Dosing Rate: 5 Ppm | Kg | 0 | 1580 | 0
4 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | No. | 1 | 2338.9831 | 2338.9831
TOTAL COST |  |  |  | (C) |  | 234538.9831
O&M Plants for 06 Months |  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 |  | A - 06 Months O&M for MF Plants - 1000 LPH | No. | 15 | 311651 | 4674765 | #REF!
2 |  | B - 06 Months O&M for RO Plants - 500 LPH | No. | 3 | 334402.9831 | 1003208.9492 | #REF!
3 |  | C - 06 Months O&M for UF Plants - 2000/4000/1000 LPH | No. | 56 | 234538.9831 | 13134183.0508
06 MONTHS O&M WITHOUT ELECTRICITY | [5 empty] | 18812157
GRAND TOTAL | [5 empty] | 18812157 | #REF!
Assistant Manager (P&MC) - CZ |  |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  |  | Punjab Aab-e-Pak Authority
Note on E8: HP: 2*5*8*30*6/1000
Note on E9: Talha Khan Niazi: 1 cip per year, 6 litr per plant per year
Note on E18: HP: 2*5*8*30*6/1000
Note on E19: Talha Khan Niazi: 1 cip per year, 6 litr per plant per year

## Electricity Charges 06 Months (hidden)
ELECTRICITY BILL FOR 06 Months MONTHS
|  | RO Electricity Charges | UF Electricity Charges | Out Standing Charges/New Connections
| Lum Sum Base Rate Per Plant /Month | 32500 | 20000 | 55000
| No of plants | 3 | 71 | 74
| Amount of Electricity for 6 months | 585000 | 8520000 | 4070000
| Amount of Electricity Charges for 06 Months | 13175000
#REF!
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authority |  | Punjab Aab-e-Pak Authority

## O&M 06
PUNJAB SAAF PANI AUTHORITY | [6 empty] | Rehab | 152
REHABILITATION & O&M OF DYSFUNCTIONAL WATER FILTRATION PLANTS INSTALLED IN DIVISON FAISALABAD
BILL OF QUANTITY
BILL NO 1 - Cost of O&M of 01 Plant for 06 Months | [6 empty] | Functional | 67
Sr. No. | Non-MRS | Description | Reverse Osmosis - 500 LPH |  |  |  | Previously Rehab | 137
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 |  | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE | No | 6
2 |  | Plant Operator, 1 Nos. | Man Months | 3 |  |  |  | Anti Scalent Calculation | 14.4
3 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2
4 |  | Antiscalent Chemical (DOSING) Dosing Rate: 5 Ppm | Kg | 3.6 |  |  |  | 7.2 | 54 | 36.4
5 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | Kg | 3 |  |  |  | 3.6 | 324 | 324 | 18
Total Cost
BILL NO 2 - Cost of O&M of 01 Plant for 06 Months
Sr. No. | Non-MRS | Description | Reverse Osmosis - 1000 LPH
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.) |  | 97.2
1 |  | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE | No | 6
2 |  | Plant Operator, 1 Nos. | Man Months | 3 |  |  |  | Anti Scalent Calculation | 14.4
3 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2
4 |  | Antiscalent Chemical (DOSING) Dosing Rate: 5 Ppm | Kg | 7.2 |  |  |  | 7.2 | 54 | 36.4
5 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | Kg | 3 |  |  |  | 3.6 | 324 | 324 | 18
Total Cost
BILL NO 3 - Cost of O&M of 01 Plant for 6 Months
Sr. No. | Non-MRS | Description | Reverse Osmosis - 2000 LPH
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.) |  | 97.2
1 |  | Jumbo Filter PPF Micro 20" Prosity 1-5 Micron Material High Pressure Plastic Melt Blown PE | No | 6
2 |  | Plant Operator, 1 Nos. | Man Months | 3 |  |  |  | Anti Scalent Calculation | 14.4
3 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2
4 |  | Antiscalent Chemical (DOSING) Dosing Rate: 5 Ppm | Kg | 14.4 |  |  |  | 7.2 | 54 | 36.4
5 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | Kg | 3 |  |  |  | 3.6 | 324 | 324 | 18
Total Cost
BILL NO 4 - Cost of O&M of 01 Plant for 06 Months
Sr. No. | Non MRS | Description | UF Plant - 2000/4000/1000 LPH
|  |  | Unit | Qty. | Unit Cost (Rs.) | Total Price (Rs.)
1 |  | Plant Operator, 1 Nos. | Man Months | 3
2 |  | Water Testing (From ISO Approved Lab) | Quarterly | 2
3 |  | Chemicals for Cleaning (CIP), Disinfection, Tank Cleaning, Site Disinfection and other cleaning material etc Acidic/Alkaline | No. | 3
Total Cost
6 Months O&M for 138 Plants |  |  | Unit | Qty. | Unit Cost | Total Price
1 |  | O&M for RO Plants - 500 LPH | No. | 5 |  |  | 6 | 14034 | 18 | 42102 | 815687.6949 | 271895.8983
2 |  | O&M for RO Plants - 1000 LPH | No. | 56 |  |  | 6 | 14034 | 114 | 266646 | 5382166.0678 | 283271.8983
3 |  | O&M for RO Plants - 2000 LPH | No. | 57
4 |  | O&M for UF Plants - 2000/4000/1000/500 LPH | No. | 20 |  |  | 6 | 14034 | 714 | 1670046 | 28845587.8983 | 242399.8983
Grand Total

## EC 06 (hidden)
ELECTRICITY BILL FOR 06 Months MONTHS
|  | RO Electricity Charges | UF / MF Electricity Charges | Out Standing Charges/New Connections
| Lum Sum Base Rate Per Plant /Month | 33500 | 20000 | 55000
| No of plants | 118 | 20 | 138 | 275.8
| Amount of Electricity for 06 months | 23718000 | 2400000 | 7590000
| TOTAL AMOUNT | 33708000
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Saaf Pani Authority |  | Punjab Saaf Pani Authority

## O&M RA (hidden)
Analysis for Non MRS Items
Quarterly Visit of Technical Team
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Charges for visit of technical person for Complete investigation and Commissioning of Water Filtration Plant | 1 | Each | 4200 | 4200
2 | Submission of Report / Fuel Allowence | 1 | P/Job | 3000 | 3000
7200
| Total |  |  |  | 7200
| Say Rupees |  |  |  | 7200
Over Head Expense / Miscellaneous
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Unseen expenditures during O&M period per month like, leakage of Pipe fittings, Repair Maintenance of Civil Work, Repair maintenance of Electrical or Mechanical Installations, Leakage of Taps or theft of taps, Log Books, Stationary etc. | 1 | Each | 8333 | 8333
2 | Carriage Market to Site / Fuel Allowence | 1 | P/Job | 0 | 0
3 | Laboure for fixing / Installation | 1 | P/Job | 0 | 0
| Contractor's Profit & Overheads 20% |  |  |  | 1666.6
| Total |  |  |  | 9999.6
| Say Rupees |  |  |  | 9999.6
CIP CHEMICAL
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | CIP Chemical Food Grade, for Cleaning of membrane, when required | 1 | Each | 2000 | 2000
| Less 18% GST |  |  |  | 305.0847
1694.9153
| Contractor's Profit & Overheads 20% |  |  |  | 338.9831
| add 18% GST |  |  |  | 305.0847
| Total |  |  |  | 2338.9831
| Say Rupees |  |  |  | 2338.9831
Quarterly Lab Test Reports
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Lab Test Reports from approved laboratories | 1 | Each | 4250 | 4250
| Less 16% PRA |  |  |  | 586.2069
2 | Transporation Charges |  |  | 450 | 450
3663.7931
| Contractor's Profit & Overheads 20% |  |  |  | 732.7586
| Total |  |  |  | 4846.5517
| Say Rupees |  |  |  | 4846.5517
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Operator Cost | [9 empty] | 450
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | As per Government Notification | 1 | Each | 32000 | 32000
| Say Rupees |  |  |  | 32000
Antiscalent - Food Grade
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Antiscalent Chemicals | 1 | Each | 1350 | 1350
| Less 17% GST |  |  |  | 196.1538
1153.8462
| Contractor's Profit & Overheads 20% |  |  |  | 230.7692
| add 17% GST |  |  |  | 196.1538
| Total |  |  |  | 1580.7692
| Say Rupees |  |  |  | 1580.7692
Sodium Hypochlorite | [6 empty] | 1000
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Sodium Hypochlorite Food Grade, for dysinfection and Chlorination, Concentration of Chlorine in Chemical 19-22% - Weight by Volume | 1 | Each | 420 | 420 | 133.3333 |  | 24 | 288 | 1.92 liter for 24 hours operation
| Less 17% GST |  |  |  | 61.0256
358.9744
| Contractor's Profit & Overheads 20% |  |  |  | 71.7949
| add 17% GST |  |  |  | 61.0256
| Total |  |  |  | 491.7949
| Say Rupees |  |  |  | 491.7949
Safety Filter Strainer | [6 empty] | 1000
Detail |  | Unit Rate for Each
|  | Qty | Unit | Rate | Amount (RS)
Material
1 | Supply and replacement of safety filter strainer | 1 | Each | 1200 | 1200 | 133.3333 |  | 24 | 288 | 1.92 liter for 24 hours operation
| Less 17% GST |  |  |  | 174.359
1025.641
| Contractor's Profit & Overheads 20% |  |  |  | 205.1282
| add 17% GST |  |  |  | 174.359
| Total |  |  |  | 1405.1282
| Say Rupees |  |  |  | 1405
Assistant Manager (P&MC) - CZ |  | Deputy Manager (P&MC) - CZ
Punjab Aab-e-Pak Authroity |  | Punjab Aab-e-Pak Authroity
Director Planning
Punjab Aab-e-Pak Authroity
Note on E40: HP: From PCRWR